## Manual
Pennsylvania Act 129 Lighting Audit and Design Tool for New Construction Projects
MANUAL
Table of Contents:
I. Purpose
II. Organization
III. User Guide
IV. Disclaimer
I. Purpose
The purpose of the Lighting Audit and Design Tool for New Construction (NC) Projects is two-fold:
1. To facilitate the calculation of eligible incentives for NC lighting projects.
2. To facilitate the calculation of energy savings and demand reduction for NC lighting projects.
II. Organization
The Lighting Audit and Design Tool for NC Projects is organized into 10 sheets.
(1) Manual
The "Manual" sheet contains the manual for using the Lighting Audit and Design Tool for NC Projects.
(2) Changelog
The "Changelog" sheet provides a brief description of major changes from the previous version.
(3) Glossary
The "Glossary" sheet is a reference defining key terms and column headings for the "Interior Lighting Form" and "Exterior Lighting Form" sheets.
(4) Interior Lighting Form
The "Interior Lighting Form" sheet is the main worksheet that calculates energy savings and peak demand reduction, following the conventions and equations described in the PA TRM. All key variables are entered on this sheet.
(5) Interior User Input
The "Interior User Input" sheet contains tables that allow additional customization of the "Interior Lighting Form" for specific cases. These tables provide the following capabilities:
Table 1: Defining "Hours of Use" and "Coincidence Factor" for the "Other" facility type. This table is required when "Other" is selected in Cell C96 of the "Interior Lighting Form" tab. Table 2: Defining a fixture wattage according to specification sheets. This table is required when (1) a fixture is not listed in the Wattage Table, or (2) the manufacturer's cut sheet indicates that the difference in delta-watts of fixture wattages (i.e. difference in delta watts of baseline and actual efficient fixture wattage and delta watts of baseline and nearest matching appendix C efficient fixture) is more than 10%.
(6) Exterior Lighting Form
The "Exterior Lighting Form" sheet is the main worksheet that calculates energy savings and peak demand reduction, following the conventions and equations described in the PA TRM. All key variables are entered on this sheet.
(7) Exterior User Input
The "Exterior User Input" sheet contains tables that allow additional customization of the "Exterior Lighting Form" for specific cases. These tables provide the following capabilities:
Table 1: Defining "Hours of Use" and "Coincidence Factor" for the "Other" facility type. This table is required when "Other" is selected in Cell C92 of the "Interior Lighting Form" tab. Table 2: Defining a fixture wattage according to specification sheets. This table is required when (1) a fixture is not listed in the Wattage Table, or (2) the manufacturer's cut sheet indicates that the difference in delta-watts of fixture wattages (i.e. difference in delta watts of baseline and actual efficient fixture wattage and delta watts of baseline and nearest matching appendix C efficient fixture) is more than 10%.
(8) Wattage Table
The "Wattage Table" sheet contains the master list of fixtures recognized by the Lighting Audit and Design Tool. The original source data is the NYSERDA Standard Wattage Table. Each fixture listed has a unique fixture code, description, and stipulated wattage value. Inclusion of a fixture in this table does not guarantee compliance with specific program requirements.
(9) Fixture Code Legend
The "Fixture Code Legend" sheet contains a legend explaining how fixture codes are constructed and how to read and identify fixture codes.
(10) Fixture Code Locator
The "Fixture Code Locator" sheet contains a tool to assist users locate a specific code on the Wattage Tables by specifying key lighting parameters. Fill in the tan fields by selecting from the pull down menu. Some fixtures in the Wattage Table may not be able to be located with this tool.
III. User Guide
1. This tool is required for new construction or building addition projects to facilitate calculation of savings pursuant to the PA TRM. This tool is optional to the EDC's EM&V contractors. The calculator contains separate “Lighting Forms” for interior and exterior applications. Each lighting form contains several tables with detailed line-by-line inventory incorporating variables required to calculate savings. The key variables required to calculate savings include building/space type, building size (gross lighted area), lighting power density (LPD), quantity and type of fixtures installed, hours of use (HOU), coincidence factors (CF) or interactive factors (IF). Consult the TRM for clarification on rules for calculating savings.
2. Begin at the "Interior Lighting Form" sheet. Complete cells C5 to C17 in the top section of the worksheet to identify the project.
3. On the "Interior Lighting Form" sheet, complete the tan sections for each line item in Tables A to E. On the "Exterior Lighting Form" sheet, complete the tan sections for each line item in Tables A to D.
4. Enter either the whole building information in Table A or the space-by-space information in Table B in tan fields in the “Interior Lighting Form” sheet. Enter the exterior area type information in Table A in tan fields in the “Exterior Lighting Form” sheet. The code lighting power density and lighting power allowance are automatically calculated.
5. Each line item in Table C of the “Interior Lighting Form” or Table B of “Exterior Lighting Form” represents fixtures in a discrete area Fixtures with different entries for any of these categories must be on separate lines. Each line entry must be definitive enough to allow verification of fixture counts in well delineated and discrete areas. Input the quantity of fixtures and fixture codes in the Table. Each fixture must be identified by a fixture code, which determines the wattage as defined by the Wattage Tables in the "Wattage Table" sheet. Codes are constructed using the legend in the "Fixture Code Legend" sheet. Users may manually search for the fixture code in the Wattage Table. Users requiring assistance identifying codes may use the tool provided in the "Fixture Code Locator" sheet. Please note the following conditions:
A) If a fixture code is not listed in the Wattage Table, a manufacturer's cut sheet (specification sheet) must be provided to determine the wattage of the associated fixture. Select the "Interior User Input" or “Exterior User Input” sheet accordingly and fill out the "Description" and "Watts/Fixture" categories for cut sheets submitted. Wattage must be easily identifiable on the cut sheet. On the "Lighting Form" sheet, fixture codes "Cut Sheet #" can now be used.
B) If the manufacturer's cut sheet indicates that the difference in delta-watts of fixture wattages (i.e. difference in delta watts of baseline and actual efficient fixture wattage and delta watts of baseline and nearest matching appendix C efficient fixture) is more than 10%, the cut sheet value may be used. Select the "User Input" sheet and fill out the "Description" and "Watts/Fixture" categories for cut sheets submitted. Wattage must be easily identifiable on the cut sheet. On the "Lighting Form" sheet, fixture codes "Cut Sheet #" can now be used.
6. Enter the lighting power allowance and program incentive offered by the EDC in tan fields in Table D of “Interior Lighting Form” or Table C of “Exterior Lighting Form”. The connected load is automatically calculated based on ASHRAE code.
7. Select the appropriate facility type in Table E of “Interior Lighting Form” or Table D of “Exterior Lighting Form” sheets from the drop down list. The corresponding Hours of Use (HOU) and Coincidence Factor (CF) values from the PA Technical Reference Manual (TRM) will be automatically loaded. These HOU and CF values will be applied to all fixtures unless the following condition applies:
A) If the facility type cannot be found in the drop down list, select "Other". On the "User Input" sheet, complete input HOU and CF for the project according to the user's best judgment and best knowledge available (e.g. facility interviews, posted schedules, or metered data). Unreasonable values are subject to adjustment by evaluators.
8. In Table E of “Interior Lighting Form” or Table D of “Exterior Lighting Form”, select the appropriate type of cooling for the space (i.e. where the fixtures are being installed).
9. For further clarification on a specific field or column, please see the "Glossary" sheet. If additional assistance is required, please contact the program manager.
10. Note that Appendix C must be used separately to calculate savings for measures other than lighting fixture installs such as control measures for NC lighting projects.
V. Disclaimer
This tool allows for custom entries for several fields. This document does not modify any requirements of the PA TRM. If any discrepancy between the TRM and this document exist, the TRM should be followed.

## Changelog
Pennsylvania Act 129 New Construction Lighting Calculator
CHANGELOG
Version 1
1) | Released with 2013 TRM Tentative Order in August 2012
Version 2
1) | Released with 2013 TRM Final Order in December 2012
Version 3 (Submitted August 29, 2013 for 2014 Tentative Order)
1) | Updated Program Years Dates in the "Interior Lighting Form" and the "Exterior Lighting Form" tabs.

## Glossary
Pennsylvania Act 129 Lighting Audit and Design Tool for New Construction Projects
GLOSSARY
Interior Lighting Form |  | Exterior Lighting Form
Project Identification |  | Project Identification
Cell C5: | "Project Application ID" is the project ID. For identification purposes. | Cell C5: | "Project Application ID" is the project ID. For identification purposes.
Cell C6: | "Customer Business Name" is the customer business name. For identification purposes. | Cell C6: | "Customer Business Name" is the customer business name. For identification purposes.
Cell C7: | "Site Address" is the address of the facility where the fixtures are being installed. For identification purposes. | Cell C7: | "Site Address" is the address of the facility where the fixtures are being installed. For identification purposes.
Cell C8: | "Site Account Number" is the EDC account number for the site. For identification purposes. | Cell C8: | "Site Account Number" is the EDC account number for the site. For identification purposes.
Cell C9: | "Customer Contact Telephone" is the customer telephone number. For identification purposes. | Cell C9: | "Customer Contact Telephone" is the customer telephone number. For identification purposes.
Cell C10: | "Customer Contact Email" is the customer email address. For identification purposes. | Cell C10: | "Customer Contact Email" is the customer email address. For identification purposes.
Cell C11: | "Customer Contact Name" is the customer contact name. For identification purposes. | Cell C11: | "Customer Contact Name" is the customer contact name. For identification purposes.
Cell C12: | "Installation Date" is the completion date of all lighting equipment. | Cell C12: | "Installation Date" is the completion date of all lighting equipment.
Cell C13: | "Utility" is the name of the utility serving the customer. | Cell C13: | "Utility" is the name of the utility serving the customer.
Cell C14: | "Survey completed by" is the name of the person who inspected the project. | Cell C14: | "Survey completed by" is the name of the person who inspected the project.
Cell C15: | "Spot Measurements completed by" is the name of the person who did spot measurements, if any. | Cell C15: | "Spot Measurements completed by" is the name of the person who did spot measurements, if any.
Cell C16: | "Date Survey completed" is the date the inspection was completed. | Cell C16: | "Date Survey completed" is the date the inspection was completed.
Cell C17: | "Program Year" is the year the project was implemented. | Cell C17: | "Program Year" is the year the project was implemented.
Lighting Power Allowance |  | Lighting Power Allowance
Cell B26: | "Building Type" is the primary function of the facility. The categories are based on the PA TRM taken from the ASHRAE 90.1-2007 manual. Select appropriate building type from the drop down list. | Cell B25: | "Exterior Area Type and Location" is the location where the lighting is installed.
Cell C26: | "Gross Lighted Area" is the total building lighted area in square feet. | Cell C25: | "ASHRAE 90.1-2007 Exterior Area Type" is the exterior space where lighting is installed. The categories are based on the PA TRM taken from the ASHRAE 90.1-2007 manual. Select appropriate building type from the drop down list.
Cell D26: | "ASHRAE 90.1-2007 Code LPD" is the code lighting power density for the building type selected in Cell B26. This value is automatically calculated.
Cell E26: | "ASHRAE 90.1-2007 Lighting Power Allowance (Baseline Power)" is the code lighting power allowance calculated based on the area entered in Cell C26 and building type selected in Cell B26. | Cell D25: | "Lighting Power Allowance Units" is the units in terms of Square Feet, Linear Feet, Number of Locations etc.
|  | Cell E25: | "Quantity associated with Exterior Area Type Lighting Power Allowance Units" is the quantity associated with the exterior area type lighting. For example, if 'Building Grounds: Walkways', enter total linear feet.
Cell B30: | "Space Type" is the location where the lighting is installed.
Cell C30: | "ASHRAE 90.1-2007 Building Area Type" is the area type where the lighting is installed. Select this from the drop down list. This method should be used where there lighting is installed in multiple areas and where there is information available regarding lighted areas for each of the space types.
|  | Cell F25: | "ASHRAE 90.1-2007 Code Exterior Lighting Power Allowance" is the code lighting power density for the space type selected in Cell C25. This value is automatically calculated.
Cell D30: | "Gross Lighted Area" is the building lighted area in square feet for a particular location. | Cell G25: | "ASHRAE 90.1-2007 Lighting Power Allowance (Baseline Power)" is the code lighting power allowance calculated based on the area entered in Cell E25 and building type selected in Cell F25.
Cell E30: | "ASHRAE 90.1-2007 Code LPD" is the code lighting power density for the space type selected in Cell B30. This value is automatically calculated.
Cell F30: | "ASHRAE 90.1-2007 Lighting Power Allowance (Baseline Power)" is the code lighting power allowance calculated based on the area entered in Cell D30 and building type selected in Cell C30.
Fixture Information
|  | Cell B45: | "Location" is the space type where lighting fixture is installed.
|  | Cell C45: | "Fixture Tag or ID" is the fixture ID number found in the electric plans, if available
Fixture Information |  | Cell D45: | "Luminaire Description" is the description of fixture and ballast (model numbers)
Cell B48: | "Location" is the space type where lighting fixture is installed. | Cell E45: | "Number of Fixtures" is the number of fixtures installed.
Cell C48: | "Fixture Tag or ID" is the fixture ID number found in the electric plans, if available | Cell F45: | "TRM Fixture Code" is the type of fixture installed. The code is selected from the "Wattage Table" sheet. If the code is unknown, the Fixture Code Locator can assist users find the correct code by filling out key parameters. If the code is not listed in the "Wattage Table" sheet, a cut sheet must be provided to determine the wattage of the associated fixture. To use cut sheets for determining wattage, "cut sheet" codes must first be defined in the "Interior User Input" sheet.
Cell D48: | "Luminaire Description" is the description of fixture and ballast (model numbers) | Cell G45: | "PA TRM Allowed Watts/Fixture" is the watts per fixture for the installed lighting. This field is populated automatically, based on the fixture code entered in Cell F48.
Cell E48: | "Number of Fixtures" is the number of fixtures installed.
Cell F48: | "TRM Fixture Code" is the type of fixture installed. The code is selected from the "Wattage Table" sheet. If the code is unknown, the Fixture Code Locator can assist users find the correct code by filling out key parameters. If the code is not listed in the "Wattage Table" sheet, a cut sheet must be provided to determine the wattage of the associated fixture. To use cut sheets for determining wattage, "cut sheet" codes must first be defined in the "Interior User Input" sheet. | Cell H45: | "Connected Watts " is the total wattage of the same fixture installed in the same area.
Cell G48: | "PA TRM Allowed Watts/Fixture" is the watts per fixture for the installed lighting. This field is populated automatically, based on the fixture code entered in Cell F48.
Incentive Information
Cell H48: | "Connected Watts " is the total wattage of the same fixture installed in the same area. | Cell B79: | "Total Building Lighting Connected Load" is the total lighting connected load for the lighting project. This is the sum of connected wattage for all fixtures for all space types. This is directly populated from the Cell H76.
Incentive Information
Cell B82: | "Total Building Lighting Connected Load" is the total lighting connected load for the lighting project. This is the sum of connected wattage for all fixtures for all space types. This is directly populated from the Cell H76. | Cell B80: | "ASHRAE 90.1-2007 Lighting Power Baseline" is the total baseline lighting connected load. This is automatically populated from Cell G40.
|  | Cell B81: | "New Construction Lighting Power Allowance" is the percentage of lighting power eligible for incentive specific to each EDC if any.
Cell B83: | "ASHRAE 90.1-2007 Lighting Power Baseline" is the total baseline lighting connected load. This is automatically calculated from Cell E27 or F43 depending on whether the method used for calculations is "Building Area Method" or "Space-by-Space Method".
|  | Cell B82: | "Maximum Lighting Power Eligible for Incentive" is the maximum amount of lighting power eligible for an incentive.
|  | Cell B83: | "Incentive YES/NO" is whether the project is eligible for an incentive or not depending on whether the project exceeds minimum code requirements.
Cell B84: | "Area or Space Method used for Baseline" is the type of method used for calculating the baseline lighting power allowance.
|  | Cell B84: | "Kilowatts Below Code" is the amount of kWh below code for the installed project.
Cell B85: | "New Construction Lighting Power Allowance" is the percentage of lighting power eligible for incentive specific to each EDC if any. | Cell B85: | "NC Program Incentive" is the amount of incentive paid by the utility.
|  | Cell B86: | "Total Incentive" is the total incentive the customer is eligible for.
Cell B86: | "Maximum Lighting Power Eligible for Incentive" is the maximum amount of lighting power eligible for an incentive.
Output Information
Cell B87: | "Incentive YES/NO" is whether the project is eligible for an incentive or not depending on whether the project exceeds minimum code requirements. | Cell B91: | "Change in Connected Load" is the difference in installed watts between the ASHRAE 90.1-2007 lighting power baseline and acutal lighting installation cases. This does not take into account coincidence factors, controls, or interactive factors.
Cell B88: | "Kilowatts Below Code" is the amount of kWh below code for the installed project.
Cell B89: | "NC Program Incentive" is the amount of incentive paid by the utility. | Cell C91: | "Facility Type" is the primary function of the facility. The categories are based on the PA TRM. "Other" should be used when no other category is sufficient.
Cell B90: | "Total Incentive" is the total incentive the customer is eligible for.
|  | Cell D91: | "Hours of Use", or "HOU", is the average annual operating hours of the baseline lighting fixture without controls.
Output Information |  | Cell E91: | "Coincidence Factor", or "CF", is the percentage of the total lighting connected load that is on during electric system’s peak period, defined as the top 100 hours.
Cell B95: | "Change in Connected Load" is the difference in installed watts between the ASHRAE 90.1-2007 lighting power baseline and acutal lighting installation cases. This does not take into account coincidence factors, controls, or interactive factors.
|  | Cell F91: | "Space Cooling Type" is the type of cooling that is used for the space in which the fixtures are being installed. This field determines the value of the interactive factors for energy and demand. The form allows for the following cooling types: Air conditioned or cooled space; Freezer space; Medium-temperature refrigerated space; High-temperature refrigerated space; Uncooled space.
Cell C95: | "Facility Type" is the primary function of the facility. The categories are based on the PA TRM. "Other" should be used when no other category is sufficient.
|  | Cell G91: | "Interactive Factor Demand" is the secondary demand reduction from cooling savings resulting from a decrease in heat generated by lighting. This applies to lighting in space that has air conditioning or refrigeration only. This factor is determined by Cell F91.
Cell D95: | "Hours of Use", or "HOU", is the average annual operating hours of the baseline lighting fixture without controls.
Cell E95: | "Coincidence Factor", or "CF", is the percentage of the total lighting connected load that is on during electric system’s peak period, defined as the top 100 hours.
|  | Cell H91: | "Interactive Factor Energy" is the secondary energy savings from cooling savings resulting from a decrease in heat generated by lighting. This applies to lighting in space that has air conditioning or refrigeration only. This factor is determined by Cell F91.
Cell F95: | "Space Cooling Type" is the type of cooling that is used for the space in which the fixtures are being installed. This field determines the value of the interactive factors for energy and demand. The form allows for the following cooling types: Air conditioned or cooled space; Freezer space; Medium-temperature refrigerated space; High-temperature refrigerated space; Uncooled space. | Cell I91: | "Peak Demand Savings" is the peak demand reduced taking into account coincidence factors, controls, and interactive factors, calculated using TRM protocols.
Cell G95: | "Interactive Factor Demand" is the secondary demand reduction from cooling savings resulting from a decrease in heat generated by lighting. This applies to lighting in space that has air conditioning or refrigeration only. This factor is determined by Cell F95. | Cell J91: | "Annual kWh Saved" is the total annual energy saved by the lighting improvement.
Cell H95: | "Interactive Factor Energy" is the secondary energy savings from cooling savings resulting from a decrease in heat generated by lighting. This applies to lighting in space that has air conditioning or refrigeration only. This factor is determined by Cell F95.
Cell I95: | "Peak Demand Savings" is the peak demand reduced taking into account coincidence factors, controls, and interactive factors, calculated using TRM protocols.
Cell J95: | "Annual kWh Saved" is the total annual energy saved by the lighting improvement.

## 01 Interior Lighting Form
New Construction Interior Lighting Incentive and Savings Calculation Worksheet | [8 empty] | Appendix E of the PA TRM
GENERAL CUSTOMER INFORMATION | [8 empty] | For instructions, see the Users Guide in the "Manual" sheet. |  |  |  | LOOKUP TABLES
Project Application ID (If Assigned):
Customer Business Name:
Site Address: | [12 empty] | Program Years in Phase II | Interior LPD Building Area Method |  | Interior LPD Space-by-Space Method
Site Account Number: | [12 empty] | Program Year 5 | Building Area Type | Watts/Sq Ft | Building Area Type | Watts/Sq Ft
Customer Contact Telephone: | [12 empty] | Program Year 6 | Automotive facility | 0.9 | Office - Enclosed | 1.1
Customer Contact Email: | [12 empty] | Program Year 7 | Convention center | 1.2 | Office - Open Plan | 1.1
Customer Contact Name: | [13 empty] | Courthouse | 1.2 | Conference/Meeting/Multi-Purpose | 1.3
Installation Date: | [13 empty] | Dining: bar lounge/leisure | 1.3 | Classroom/Lecture/Training | 1.4
Utility: | [12 empty] | Utility | Dining: cafeteria/fast food | 1.4 | Classroom/Lecture/Training - For Penitentiary | 1.3
Survey completed by (name): | [12 empty] | Duquesne Light | Dining: family | 1.6 | Lobby | 1.3
Spot Measurements completed by (name): | [12 empty] | Met-Ed (FirstEnergy) | Dormitory | 1 | Lobby - For Hotel | 1.1
Date(s) Survey completed: | [12 empty] | Penn Power (FirstEnergy) | Exercise center | 1 | Lobby - For Performing Arts Center | 3.3
Program Year: | [12 empty] | PennElec (FirstEnergy) | Gymnasium | 1.1 | Lobby - For Motion Picture Theater | 1.1
[13 empty] | West Penn Power (FirstEnergy) | Health-care clinic | 1 | Audience Seating Area | 0.9
| Input Field | [11 empty] | PECO | Hospital | 1.2 | Audience Seating Area - For Gymnasium | 0.4
| Computed Field | [11 empty] | PPL | Hotel | 1 | Audience Seating Area - For Exercise Center | 0.3
[14 empty] | Library | 1.3 | Audience Seating Area - For Convention Center | 0.7
ENTER EITHER THE WHOLE BUILDING INFORMATION IN TABLE (A) OR THE SPACE-BY-SPACE INFORMATION IN TABLE (B) BELOW | [13 empty] | Manufacturing facility | 1.3 | Audience Seating Area - For Penitentiary | 0.7
[10 empty] | Space Type | Abbrv. | IF_Demand | IF_Energy | Motel | 1 | Audience Seating Area - For Religious Buildings | 1.7
[10 empty] | Air Conditioned/Cooled space (610F - 790F) | COOL | 0.34 | 0.12 | Motion picture theater | 1.2 | Audience Seating Area - For Sports Arenas | 0.4
Table A. ASHRAE 90.1-2007 Lighting Power Allowance Using the Building Area Method | [9 empty] | Freezer space (-200F - 270F) | FREZ | 0.5 | 0.5 | Multifamily | 0.7 | Audience Seating Area - For Performing Arts Theater | 2.6
Building Type | Gross Lighted Area (ft2) | ASHRAE 90.1-2007 Code LPD (W/ft2) | ASHRAE 90.1-2007 Lighting Power Allowance (Baseline Power) (W) | [6 empty] | Medium-temperature refrigerated space (280F - 400F) | MTRF | 0.29 | 0.29 | Museum | 1.1 | Audience Seating Area - For Motion Picture Theater | 1.2
[10 empty] | High-temperature refrigerated space (410F - 600F) | HTRF | 0.18 | 0.18 | Office | 1 | Audience Seating Area - For Transportation | 0.5
[10 empty] | Uncooled space | UNCL | 0 | 0 | Parking garage | 0.3 | Atrium - First Three Floors | 0.6
Table B. ASHRAE 90.1-2007 Lighting Power Allowance Using the Space-by-Space Method | [13 empty] | Penitentiary | 1 | Atrium - Each Additional Floor | 0.2
Space Type | ASHRAE 90.1-2007 Building Area Type | Gross Lighted Area | ASHRAE 90.1-2007 Code Lighting Power Density Allowance (W/ft2) | ASHRAE 90.1-2007 Lighting Power Allowance (Baseline Power) (W) | [9 empty] | Performing arts theater | 1.6 | Lounge/Recreation | 1.2
Example: Dining Area | Dining Area - For Hotel | 1000 | 1.3 | 1300 | [9 empty] | Police/fire station | 1 | Lounge/Recreation - For Hospital | 0.8
[14 empty] | Post office | 1.1 | Dining Area | 0.9
[14 empty] | Religious building | 1.3 | Dining Area - For Penitentiary | 1.3
[14 empty] | Retail | 1.5 | Dining Area - For Hotel | 1.3
[14 empty] | School/university | 1.2 | Dining Area - For Motel | 1.2
[14 empty] | Sports arena | 1.1 | Dining Area - For Bar Lounge/Leisure Dining | 1.4
[14 empty] | Town hall | 1.1 | Dining Area - For Family Dining | 2.1
[14 empty] | Transportation | 1 | Food Preparation | 1.2
[14 empty] | Warehouse | 0.8 | Laboratory | 1.4
[14 empty] | Workshop | 1.4 | Restrooms | 0.9
[16 empty] | Dressing/Locker/Fitting Room | 0.6
[16 empty] | Corridor/Transition | 0.5
[16 empty] | Corridor/Transition - For Hospital | 1
[16 empty] | Corridor/Transition - For Manufacturing Facility | 0.5
[16 empty] | Stairs - Active | 0.6
[16 empty] | Active Storage | 0.8
Table C: Installed Lighting Equipment Power: Enter Information for ALL new light fixtures | [15 empty] | Active Storage - For Hospital | 0.9
Location | Fixture Tag or ID | Luminaire Description | Number of Fixtures of this type | TRM Fixture Code | PA TRM Allowed Watts/Fixture | Connected Watts | [9 empty] | Inactive Storage | 0.3
EXAMPLE: Sales (General ) | A/A1 | 2ES8 232 2x4, 2L 32W, QHE-ISN 2x32 | 155 | F42ILL | 59 | 9145 | [9 empty] | Inactive Storage - For Museum | 0.8
[16 empty] | Electrical/Mechanical | 1.5
[16 empty] | Workshop | 1.9
[16 empty] | Sales Area | 1.7
[16 empty] | Gymnasium/Exercise Center - Playing Area | 1.4
[16 empty] | Gymnasium/Exercise Center - Exercise Area | 0.9
[16 empty] | Courthouse/Police Station/Penitentiary - Courtroom | 1.9
[16 empty] | Courthouse/Police Station/Penitentiary - Confinement Cells | 0.9
[16 empty] | Courthouse/Police Station/Penitentiary - Judges' Chambers | 1.3
[16 empty] | Fire Stations - Engine Room | 0.8
[16 empty] | Fire Stations - Sleeping Quarters | 0.3
[16 empty] | Post Office - Sorting Area | 1.2
[16 empty] | Convention Center Exhibit Space | 1.3
[16 empty] | Library - Card File and Cataloging | 1.1
[16 empty] | Library - Stacks | 1.7
[16 empty] | Library - Reading Area | 1.2
[16 empty] | Hospital - Emergency | 2.7
[16 empty] | Hospital - Recovery | 0.8
[16 empty] | Hospital - Nurses' Station | 1
[16 empty] | Hospital - Exam/Treatment | 1.5
[16 empty] | Hospital - Pharmacy | 1.2
[16 empty] | Hospital - Patient Room | 0.7
[16 empty] | Hospital - Operating Room | 2.2
[16 empty] | Hospital - Nursery | 0.6
[16 empty] | Hospital - Medical Supply | 1.4
[16 empty] | Hospital - Physical Therapy | 0.9
[16 empty] | Hospital - Radiology | 0.4
[16 empty] | Hospital - Laundry - Washing | 0.6
[16 empty] | Automotive - Service/Repair | 0.7
[16 empty] | Manufacturing - Low Bay (<25Ft Fl. to Ceiling Height) | 1.2
Total Installed Lighting Power (Watts) | [15 empty] | Manufacturing - High Bay (≥25Ft Fl. to Ceiling Height) | 1.7
[16 empty] | Manufacturing - Detailed Manufacturing | 2.1
Table D: Incentive Estimate Calculation | [15 empty] | Manufacturing - Equipment Room | 1.2
Total Building Lighting Connected Load (watts) | [15 empty] | Manufacturing - Control Room | 0.5
ASHRAE 90.1-2007 Lighting Power Baseline (W) | [15 empty] | Hotel/Motel Guest Rooms | 1.1
Area or Space Method used for Baseline | [15 empty] | Dormitory - Living Quarters | 1.1
New Construction Lighting Power Allowance | [15 empty] | Museum - General Exhibition | 1
Maximum Lighting Power Eligible for Incentive (W) | [15 empty] | Museum - Restoration | 1.7
Incentive YES/NO | [15 empty] | Bank/Office-Banking Activity Area | 1.5
Kilowatts Below Code | [15 empty] | Religious Buildings - Worship Pulpit, Choir | 2.4
NC Program Incentive ($/kW below Code) | [15 empty] | Religious Buildings - Fellowship Hall | 0.9
Total Incentive | [15 empty] | Retail - Sales Area | 1.7
[16 empty] | Retail - Mall Concourse | 1.7
[16 empty] | Sports Arenas - Ring Sports Area | 2.7
[16 empty] | Sports Arenas - Court Sports Area | 2.3
Table E: TRM Savings Calculation | [15 empty] | Sports Arenas - Indoor Playing Field Area | 1.4
Change in Connected Load based on ASHRAE 90.1-2007 Code (kW) | Facility Type | HOU | Coincidence Factor | Predominant Space Cooling Type | Interactive Factor (demand) | Interactive Factor (energy) | Peak Demand Savings (kW) | Annual kWh Saved | [7 empty] | Warehouse - Fine Material Storage | 1.4
[16 empty] | Warehouse - Medium/Bulky Material Storage | 0.9
[16 empty] | Parking Garage - Garage Area | 0.2
[16 empty] | Transportation - Airport - Concourse | 0.6
[16 empty] | Transportation - Air/Train/Bus - Baggage Area | 1
[16 empty] | Transportation - Terminal Ticket Counter | 1.5
Note on D13: Utility: Select the utility serving the facility from the pull down menu.
Note on D17: Program Year: Program Year 5: June 1, 2013 - May 31, 2014 Program Year 6: June 1, 2014 - May 31, 2015 Program Year 7: June 1, 2015 - May 31, 2016
Note on B26: Select the closest building type from the Lookup Table in the cell below
Note on C26: Enter the Total Building Lighted Area in Square Feet
Note on B30: Describe the area or source of fixture count
Note on C30: Select Area Type from Table that best describes the area use : Refer to Tab 'Space-by-Space LPD Table'
Note on D30: Enter Lighted Area in Square Feet (ft2)
Note on B47: Fixtures exempted by Code do not need to be entered
Note on B48: Space Type where fixture is installed
Note on C48: From Electric Plans if Available
Note on D48: Enter theDescription of Fixture
Note on E48: Enter Quantity
Note on F48: Enter from TAB 'Wattage Table'
Note on D85: Enter percentage of lighting power eligible for incentive depending on the EDC if any.
Note on D89: Enter EDC program incentive per kW below code
Note on D95: if 'Other' Facility Type, provide HOU and CF in 'Int User Input' tab. Data supporting other hours must be provided.

## 02 Interior User Input
Defining HOU and CF for "Other" Facility Type |  |  | Defining Wattages for Fixtures not in the Wattage Table or Exceptional Cases
Facility Type | HOU | CF | Fixture Code | Description | Watts/Fixture
Auto Related | 4056 | 0.62 | Cut Sheet 1 | Edit | Edit
Daycare | 2590 | 0.62 | Cut Sheet 2 | Edit | Edit
Education – School | 1632 | 0.31 | Cut Sheet 3 | Edit | Edit
Education – College/University | 2348 | 0.76 | Cut Sheet 4 | Edit | Edit
Grocery | 4660 | 0.87 | Cut Sheet 5 | Edit | Edit
Health/Medical – Clinic | 3213 | 0.73 | Cut Sheet 6 | Edit | Edit
Hospitals | 5182 | 0.8 | Cut Sheet 7 | Edit | Edit
Industrial Manufacturing – 1 Shift | 2857 | 0.57 | Cut Sheet 8 | Edit | Edit
Industrial Manufacturing – 2 Shift | 4730 | 0.57 | Cut Sheet 9 | Edit | Edit
Industrial Manufacturing – 3 Shift | 6631 | 0.57 | Cut Sheet 10 | Edit | Edit
Libraries | 2566 | 0.62 | Cut Sheet 11 | Edit | Edit
Lodging – Guest Rooms | 914 | 0.09 | Cut Sheet 12 | Edit | Edit
Lodging – Common Spaces | 7884 | 0.9 | Cut Sheet 13 | Edit | Edit
Multi-Family (Common Areas) - High-rise & Low-rise | 5950 | 0.62 | Cut Sheet 14 | Edit | Edit
Nursing Home | 4160 | 0.62 | Cut Sheet 15 | Edit | Edit
Office | 2567 | 0.61 | Cut Sheet 16 | Edit | Edit
Parking Garages | 6552 | 0.62 | Cut Sheet 17 | Edit | Edit
Public Order and Safety | 5366 | 0.62 | Cut Sheet 18 | Edit | Edit
Public Assembly (one shift) | 2610 | 0.62 | Cut Sheet 19 | Edit | Edit
Public Services (nonfood) | 3425 | 0.62 | Cut Sheet 20 | Edit | Edit
Restaurant | 3613 | 0.65
Retail | 2829 | 0.73
Religious Worship/Church | 1810 | 0.62
Storage Conditioned/Unconditioned | 3420 | 0.62
Warehouse | 2316 | 0.54
Other (Fill in "User Input" sheet) | Edit | Edit

## 03 Exterior Lighting Form
New Construction Exterior Lighting Incentive and Savings Calculation Worksheet | [8 empty] | Appendix E of the PA TRM
GENERAL CUSTOMER INFORMATION | [8 empty] | For instructions, see the Users Guide in the "Manual" sheet.
Project Application ID (If Assigned):
Customer Business Name:
Site Address:
Site Account Number: | [9 empty] | LOOKUP TABLES
Customer Contact Telephone:
Customer Contact Email:
Customer Contact Name: | [9 empty] | Program Years in Phase II
Installation Date: | [9 empty] | Program Year 5
Utility: | [9 empty] | Program Year 6
Survey completed by (name): | [9 empty] | Program Year 7
Spot Measurements completed by (name):
Date(s) Survey completed:
Program Year: | [9 empty] | Utility
Duquesne Light
| Input Field | [8 empty] | Met-Ed (FirstEnergy)
| Computed Field | [8 empty] | Penn Power (FirstEnergy) | EXTERIOR LIGHTING POWER ALLOWANCE TABLE
[10 empty] | PennElec (FirstEnergy) | Building Exterior and Space Description | Allowance | Variable | Units
ENTER THE REQUESTED INFORMATION IN TABLE (A) BELOW | [9 empty] | West Penn Power (FirstEnergy) | Uncovered Parking Area: Parking Lots and Drives | 0.15 | Square Feet | W/ft2
[10 empty] | PECO | Building Grounds: Walkways less than 10 ft wide | 1 | Linear Feet | W/linear foot
Table A. ASHRAE 90.1 2007 Lighting Power Allowance | [9 empty] | PPL | Building Grounds: Walkways 10 ft wide or greater | 0.2 | Square Feet | W/ft2
Exterior Area Type and Location | ASHRAE 90.1-2007 Exterior Area Type | Lighting Power Allowance Units | Quantity associated with Exterior Area Type Lighting Power Allowance Units | ASHRAE 90.1-2007 Code Exterior Lighting Power Allowance | ASHRAE 90.1-2007 Lighting Power Allowance (Baseline Power) (W) | [5 empty] | Building Grounds: Plaza areas | 0.2 | Square Feet | W/ft2
Example | Building Grounds: Walkways less than 10 ft wide | Linear Feet | 1000 | 1 | 1000 | [5 empty] | Building Grounds: Special feature areas | 0.2 | Square Feet | W/ft2
[11 empty] | Building Grounds: Stairways | 1 | Square Feet | W/ft2
[11 empty] | Building Entrances and Exits: Main entries | 30 | Door Width (Linear Feet) | W/linear foot of door width
[11 empty] | Building Entrances and Exits: Other doors | 20 | Door Width (Linear Feet) | W/linear foot of door width
[11 empty] | Canopies and Overhangs: Free standing and attached overhangs | 1.25 | Square Feet | W/ft2
[11 empty] | Outdoor sales: Open Areas (including vehicle sales lots) | 0.5 | Square Feet | W/ft2
[11 empty] | Outdoor sales: Street frontage for vehicle sales in addition to "open area" allowance | 20 | Linear Feet | W/linear foot
[11 empty] | Building Facades: per illuminated wall or surface area | 0.2 | Square Feet | W/ft2 for each illuminated wall or surface
[11 empty] | Building Facades: per illuminated wall or surface length | 5 | Linear Feet | W/linear foot for each illuminated wall or surface length
[11 empty] | Automated teller machines and night depositories: per first location | 270 | Watts per Location | W per location
[11 empty] | Automated teller machines and night depositories: per additional locations | 90 | Watts per Location | W per additional ATM per location
[11 empty] | Entrances and gatehouse inspection stations at guarded facilities | 1.25 | Square Feet | W/ft2 of uncovered area
[11 empty] | Loading areas for law enforcement, fire, ambulance, and other emergency service vehicles | 0.5 | Square Feet | W/ft2 of uncovered area
[11 empty] | Drive-through windows at fast food restaurants | 400 | Watts per Location | W per drive-through
[11 empty] | Parking near 24-hour retail entrances | 800 | Watts per Location | W per main entry
Table B. Installed Lighting Equipment Power: Enter Information for ALL new light fixtures
Location | Fixture Tag or ID | Luminaire Description | Number of Fixtures of this type | TRM Fixture Code | PA TRM Allowed Watts/Fixture | Connected Watts
Example | W1 | 320 W Pulse Start MH | 20 | MHPS/LR/320/1 | 349 | 6980
Total Installed Lighting Power (Watts)
Table C. Incentive Estimate Calculation
Total Lighting Connected Load (watts)
ASHRAE 90.1-2007 Lighting Power Baseline (W)
New Construction Lighting Power Allowance
Maximum Lighting Power Eligible for Incentive (W)
Incentive YES/NO
Kilowatts Below Code
NC Program Incentive ($/kW below Code)
Total Incentive
Table D. TRM Savings Calculation
Change in Connected Load based on ASHRAE 90.1-2007 Code (kW) | Facility Type | HOU | Coincidence Factor | Predominant Space Cooling Type | Interactive Factor (demand) | Interactive Factor (energy) | Peak Demand Savings (kW) | Annual kWh Saved
|  |  |  | UNCL | 0 | 0
Note on D13: Utility: Select the utility serving the facility from the pull down menu.
Note on D17: Program Year: Program Year 5: June 1, 2013 - May 31, 2014 Program Year 6: June 1, 2014 - May 31, 2015 Program Year 7: June 1, 2015 - May 31, 2016
Note on B25: Describe the area and location
Note on C25: Select area type that best describes the area use
Note on D25: Units in terms of Square Feet, Linear Feet, Number of Locations
Note on E25: Enter the quantity associated with the exterior area type lighting. For example, if 'Building Grounds: Walkways', enter total linear feet
Note on B44: Fixtures exempted by Code do not need to be entered
Note on B45: Space Type where fixture is installed
Note on C45: From Electric Plans if Available
Note on D45: Enter Your Description of Fixture
Note on E45: Enter Quantity
Note on F45: Enter from TAB 'Wattage Table'
Note on D81: Enter percentage of lighting power eligible for incentive depending on the EDC if any.
Note on D85: Enter EDC program incentive per kW below code
Note on D91: if 'Other' Facility Type is selected, provide HOU and CF in 'Exterior User Input' tab. Data supporting other hours must be provided.

## 04 Exterior User Input
Defining HOU and CF for "Other" Facility Type |  |  | Defining Wattages for Fixtures not in the Wattage Table or Exceptional Cases
Facility Type | HOU | CF | Fixture Code | Description | Watts/Fixture
Dusk-to-Dawn / Exterior Lighting | 3833 | 0 | Cut Sheet 1 | Edit | Edit
24/7 Facilities or Spaces | 8760 | 1 | Cut Sheet 2 | Edit | Edit
Other | Edit | Edit | Cut Sheet 3 | Edit | Edit
|  |  | Cut Sheet 4 | Edit | Edit
|  |  | Cut Sheet 5 | Edit | Edit
|  |  | Cut Sheet 6 | Edit | Edit
|  |  | Cut Sheet 7 | Edit | Edit
|  |  | Cut Sheet 8 | Edit | Edit
|  |  | Cut Sheet 9 | Edit | Edit
|  |  | Cut Sheet 10 | Edit | Edit
|  |  | Cut Sheet 11 | Edit | Edit
|  |  | Cut Sheet 12 | Edit | Edit
|  |  | Cut Sheet 13 | Edit | Edit
|  |  | Cut Sheet 14 | Edit | Edit
|  |  | Cut Sheet 15 | Edit | Edit
|  |  | Cut Sheet 16 | Edit | Edit
|  |  | Cut Sheet 17 | Edit | Edit
|  |  | Cut Sheet 18 | Edit | Edit
|  |  | Cut Sheet 19 | Edit | Edit
|  |  | Cut Sheet 20 | Edit | Edit

## 06 Wattage Table
Pennsylvania Act 129 Lighting Audit and Design Tool for New Construction Projects
WATTAGE TABLE
FIXTURE CODE | LAMP CODE | DESCRIPTION | BALLAST | LAMP / FIXT | WATT / LAMP | INTERIOR WATT / FIXT | EXTERIOR WATT / FIXT
Compact Fluorescent Light Fixtures
CF10/2D | CFD10W | Compact Fluorescent, 2D, (1) 10W lamp | Mag-STD | 1 | 10 | 16 | 16
CF10/2D-L | CFD10W | Compact Fluorescent, 2D, (1) 10W lamp | Electronic | 1 | 10 | 12 | 12
CF11/1 | CF11W | Compact Fluorescent, (1) 11W lamp | Mag-STD | 1 | 11 | 13 | 13
CF11/2 | CF11W | Compact Fluorescent, (2) 11W lamp | Mag-STD | 2 | 11 | 26 | 26
CF16/2D | CFD16W | Compact Fluorescent, 2D, (1) 16W lamp | Mag-STD | 1 | 16 | 26 | 26
CF16/2D-L | CFD16W | Compact Fluorescent, 2D, (1) 16W lamp | Electronic | 1 | 16 | 18 | 18
CF18/3-L | CF18W | Compact Fluorescent, (3) 18W lamp | Electronic | 3 | 18 | 60 | 60
CF21/2D | CFD21W | Compact Fluorescent, 2D, (1) 21W lamp | Mag-STD | 1 | 21 | 26 | 26
CF21/2D-L | CFD21W | Compact Fluorescent, 2D, (1) 21W lamp | Electronic | 1 | 21 | 22 | 22
CF23/1 | CF23W | Compact Fluorescent, (1) 23W lamp | Mag-STD | 1 | 23 | 29 | 29
CF23/1-L | CF23W | Compact Fluorescent, (1) 23W lamp | Electronic | 1 | 23 | 25 | 25
CF26/3-L | CF26W | Compact Fluorescent, (3) 26W lamp | Electronic | 3 | 26 | 82 | 82
CF26/4-L | CF26W | Compact Fluorescent, (4) 26W lamp | Electronic | 4 | 26 | 108 | 108
CF26/6-L | CF26W | Compact Fluorescent, (6) 26W lamp | Electronic | 6 | 26 | 162 | 162
CF26/8-L | CF26W | Compact Fluorescent, (8) 26W lamp | Electronic | 8 | 26 | 216 | 216
CF28/2D | CFD28W | Compact Fluorescent, 2D, (1) 28W lamp | Mag-STD | 1 | 28 | 35 | 35
CF28/2D-L | CFD28W | Compact Fluorescent, 2D, (1) 28W lamp | Electronic | 1 | 28 | 28 | 28
CF32/3-L | CF32W | Compact Fluorescent, (3) 32W lamp | Electronic | 3 | 32 | 114 | 114
CF32/4-L | CF32W | Compact Fluorescent, (4) 32W lamp | Electronic | 4 | 32 | 152 | 152
CF32/6-L | CF32W | Compact Fluorescent, (6) 32W lamp | Electronic | 6 | 32 | 228 | 228
CF32/8-L | CF32W | Compact Fluorescent, (8) 32W lamp | Electronic | 8 | 32 | 304 | 304
CF38/2D | CFD38W | Compact Fluorescent, 2D, (1) 38W lamp | Mag-STD | 1 | 38 | 46 | 46
CF38/2D-L | CFD38W | Compact Fluorescent, 2D, (1) 38W lamp | Electronic | 1 | 38 | 36 | 36
CF42/1-L | CF42W | Compact Fluorescent, (1) 42W lamp | Electronic | 1 | 42 | 48 | 48
CF42/2-L | CF42W | Compact Fluorescent, (2) 42W lamp | Electronic | 2 | 42 | 100 | 100
CF42/3-L | CF42W | Compact Fluorescent, (3) 42W lamp | Electronic | 3 | 42 | 141 | 141
CF42/4-L | CF42W | Compact Fluorescent, (4) 42W lamp | Electronic | 4 | 42 | 188 | 188
CF42/6-L | CF42W | Compact Fluorescent, (6) 42W lamp | Electronic | 6 | 42 | 282 | 282
CF42/8-L | CF42W | Compact Fluorescent, (8) 42W lamp | Electronic | 8 | 42 | 376 | 376
CFQ10/1 | CFQ10W | Compact Fluorescent, quad, (1) 10W lamp | Mag-STD | 1 | 10 | 15 | 15
CFQ13/1 | CFQ13W | Compact Fluorescent, quad, (1) 13W lamp | Mag-STD | 1 | 13 | 17 | 17
CFQ13/1-L | CFQ13W | Compact Fluorescent, quad, (1) 13W lamp, BF=1.05 | Electronic | 1 | 13 | 15 | 15
CFQ13/2 | CFQ13W | Compact Fluorescent, quad, (2) 13W lamp | Mag-STD | 2 | 13 | 31 | 31
CFQ13/2-L | CFQ13W | Compact Fluorescent, quad, (2) 13W lamp, BF=1.0 | Electronic | 2 | 13 | 28 | 28
CFQ13/3 | CFQ13W | Compact Fluorescent, quad, (3) 13W lamp | Mag-STD | 3 | 13 | 48 | 48
CFQ15/1 | CFQ15W | Compact Fluorescent, quad, (1) 15W lamp | Mag-STD | 1 | 15 | 20 | 20
CFQ17/1 | CFQ17W | Compact Fluorescent, quad, (1) 17W lamp | Mag-STD | 1 | 17 | 24 | 24
CFQ17/2 | CFQ17W | Compact Fluorescent, quad, (2) 17W lamp | Mag-STD | 2 | 17 | 48 | 48
CFQ18/1 | CFQ18W | Compact Fluorescent, quad, (1) 18W lamp | Mag-STD | 1 | 18 | 26 | 26
CFQ18/1-L | CFQ18W | Compact Fluorescent, quad, (1) 18W lamp, BF=1.0 | Electronic | 1 | 18 | 20 | 20
CFQ18/2 | CFQ18W | Compact Fluorescent, quad, (2) 18W lamp | Mag-STD | 2 | 18 | 45 | 45
CFQ18/2-L | CFQ18W | Compact Fluorescent, quad, (2) 18W lamp, BF=1.0 | Electronic | 2 | 18 | 38 | 38
CFQ18/4 | CFQ18W | Compact Fluorescent, quad, (4) 18W lamp | Mag-STD | 4 | 18 | 90 | 90
CFQ20/1 | CFQ20W | Compact Fluorescent, quad, (1) 20W lamp | Mag-STD | 1 | 20 | 23 | 23
CFQ20/2 | CFQ20W | Compact Fluorescent, quad, (2) 20W lamp | Mag-STD | 2 | 20 | 46 | 46
CFQ22/1 | CFQ22W | Compact Fluorescent, quad, (1) 22W lamp | Mag-STD | 1 | 22 | 24 | 24
CFQ22/2 | CFQ22W | Compact Fluorescent, quad, (2) 22W lamp | Mag-STD | 2 | 22 | 48 | 48
CFQ22/3 | CFQ22W | Compact Fluorescent, quad, (3) 22W lamp | Mag-STD | 3 | 22 | 72 | 72
CFQ25/1 | CFQ25W | Compact Fluorescent, quad, (1) 25W lamp | Mag-STD | 1 | 25 | 33 | 33
CFQ25/2 | CFQ25W | Compact Fluorescent, quad, (2) 25W lamp | Mag-STD | 2 | 25 | 66 | 66
CFQ26/1 | CFQ26W | Compact Fluorescent, quad, (1) 26W lamp | Mag-STD | 1 | 26 | 33 | 33
CFQ26/1-L | CFQ26W | Compact Fluorescent, quad, (1) 26W lamp, BF=0.95 | Electronic | 1 | 26 | 27 | 27
CFQ26/2 | CFQ26W | Compact Fluorescent, quad, (2) 26W lamp | Mag-STD | 2 | 26 | 66 | 66
CFQ26/2-L | CFQ26W | Compact Fluorescent, quad, (2) 26W lamp, BF=0.95 | Electronic | 2 | 26 | 50 | 50
CFQ26/3 | CFQ26W | Compact Fluorescent, quad, (3) 26W lamp | Mag-STD | 3 | 26 | 99 | 99
CFQ26/6-L | CFQ26W | Compact Fluorescent, quad, (6) 26W lamp, BF=0.95 | Electronic | 6 | 26 | 150 | 150
CFQ28/1 | CFQ28W | Compact Fluorescent, quad, (1) 28W lamp | Mag-STD | 1 | 28 | 33 | 33
CFQ9/1 | CFQ9W | Compact Fluorescent, quad, (1) 9W lamp | Mag-STD | 1 | 9 | 14 | 14
CFQ9/2 | CFQ9W | Compact Fluorescent, quad, (2) 9W lamp | Mag-STD | 2 | 9 | 23 | 23
CFS7/1 | CFS7W | Compact Fluorescent, spiral, (1) 7W lamp | Electronic | 1 | 7 | 7 | 7
CFS9/1 | CFS9W | Compact Fluorescent, spiral, (1) 9W lamp | Electronic | 1 | 9 | 9 | 9
CFS11/1 | CFS11W | Compact Fluorescent, spiral, (1) 11W lamp | Electronic | 1 | 11 | 11 | 11
CFS13/1 | CFS13W | Compact Fluorescent, spiral, (1) 13W lamp | Electronic | 1 | 13 | 13 | 13
CFS15/1 | CFS15W | Compact Fluorescent, spiral, (1) 15W lamp | Electronic | 1 | 15 | 15 | 15
CFS20/1 | CFS20W | Compact Fluorescent, spiral, (1) 20W lamp | Electronic | 1 | 20 | 20 | 20
CFS23/1 | CFS23W | Compact Fluorescent, spiral, (1) 23W lamp | Electronic | 1 | 23 | 23 | 23
CFS26/1 | CFS26W | Compact Fluorescent, spiral, (1) 26W lamp | Electronic | 1 | 26 | 26 | 26
CFS27/1 | CFS27W | Compact Fluorescent, spiral, (1) 27W lamp | Electronic | 1 | 27 | 27 | 27
CFT13/1 | CFT13W | Compact Fluorescent, twin, (1) 13W lamp | Mag-STD | 1 | 13 | 17 | 17
CFT13/2 | CFT13W | Compact Fluorescent, twin, (2) 13W lamp | Mag-STD | 2 | 13 | 31 | 31
CFT13/3 | CFT13W | Compact Fluorescent, twin, (3) 13 W lamp | Mag-STD | 3 | 13 | 48 | 48
CFT18/1 | CFT18W | Compact Fluorescent, long twin., (1) 18W lamp | Mag-STD | 1 | 18 | 24 | 24
CFT22/1 | CFT22W | Compact Fluorescent, twin, (1) 22W lamp | Mag-STD | 1 | 22 | 27 | 27
CFT22/2 | CFT22W | Compact Fluorescent, twin, (2) 22W lamp | Mag-STD | 2 | 22 | 54 | 54
CFT22/4 | CFT22W | Compact Fluorescent, twin, (4) 22W lamp | Mag-STD | 4 | 22 | 108 | 108
CFT24/1 | CFT24W | Compact Fluorescent, long twin, (1) 24W lamp | Mag-STD | 1 | 24 | 32 | 32
CFT28/1 | CFT28W | Compact Fluorescent, twin, (1) 28W lamp | Mag-STD | 1 | 28 | 33 | 33
CFT28/2 | CFT28W | Compact Fluorescent, twin, (2) 28W lamp | Mag-STD | 2 | 28 | 66 | 66
CFT32/1-L | CFM32W | Compact Fluorescent, twin or multi, (1) 32W lamp | Electronic | 1 | 32 | 34 | 34
CFT32/2-L | CFM32W | Compact Fluorescent, twin or multi, (2) 32W lamp | Electronic | 2 | 32 | 62 | 62
CFT32/6-L | CFM32W | Compact Fluorescent, twin or multi, (6) 32W lamp | Electronic | 6 | 32 | 186 | 186
CFT36/1 | CFT36W | Compact Fluorescent, long twin, (1) 36W lamp | Mag-STD | 1 | 36 | 51 | 51
CFT36/4-BX | CFT36W | Compact Fluorescent, Biax, (4) 36W lamp | Electronic | 4 | 36 | 148 | 148
CFT36/6-BX | CFT36W | Compact Fluorescent, Biax, (6) 36W lamp | Electronic | 6 | 36 | 212 | 212
CFT36/6-L | CFT36W | Compact Fluorescent, long Twin, (6) 36W lamp | Electronic | 6 | 36 | 198 | 198
CFT36/6-LH | CFT36W | Compact Fluorescent, long Twin, (6) 36W lamp/ High Ballast Factor | Electronic | 6 | 36 | 210 | 210
CFT36/8-BX | CFT36W | Compact Fluorescent, Biax, (8) 36W lamp | Electronic | 8 | 36 | 296 | 296
CFT36/8-L | CFT36W | Compact Fluorescent, long Twin, (8) 36W lamp | Electronic | 8 | 36 | 270 | 270
CFT36/8-LH | CFT36W | Compact Fluorescent, long Twin, (8) 36W lamp/ High Ballast Factor | Electronic | 8 | 36 | 286 | 286
CFT36/9-BX | CFT36W | Compact Fluorescent, Biax, (9) 36W lamp | Electronic | 9 | 36 | 318 | 318
CFT40/1 | CFT40W | Compact Fluorescent, twin, (1) 40W lamp | Mag-STD | 1 | 40 | 46 | 46
CFT40/12-BX | CFT40W | Compact Fluorescent, Biax, (12) 40W lamp | Electronic | 12 | 40 | 408 | 408
CFT40/1-BX | CFT40W | Compact Fluorescent, Biax, (1) 40W lamp | Electronic | 1 | 40 | 46 | 46
CFT40/1-L | CFT40W | Compact Fluorescent, long twin, (1) 40W lamp | Electronic | 1 | 40 | 43 | 43
CFT40/2 | CFT40W | Compact Fluorescent, twin, (2) 40W lamp | Mag-STD | 2 | 40 | 85 | 85
CFT40/2-BX | CFT40W | Compact Fluorescent, Biax, (2) 40W lamp | Electronic | 2 | 40 | 72 | 72
CFT40/2-L | CFT40W | Compact Fluorescent, long twin, (2) 40W lamp | Electronic | 2 | 40 | 72 | 72
CFT40/3 | CFT40W | Compact Fluorescent, twin, (3) 40 W lamp | Mag-STD | 3 | 40 | 133 | 133
CFT40/3-BX | CFT40W | Compact Fluorescent, Biax, (3) 40W lamp | Electronic | 3 | 40 | 102 | 102
CFT40/3-L | CFT40W | Compact Fluorescent, long twin, (3) 40W lamp | Electronic | 3 | 40 | 105 | 105
CFT40/4-BX | CFT40W | Compact Fluorescent, Biax, (4) 40W lamp | Electronic | 4 | 40 | 144 | 144
CFT40/5-BX | CFT40W | Compact Fluorescent, Biax, (5) 40W lamp | Electronic | 5 | 40 | 190 | 190
CFT40/6-BX | CFT40W | Compact Fluorescent, Biax, (6) 40W lamp | Electronic | 6 | 40 | 204 | 204
CFT40/6-L | CFT40W | Compact Fluorescent, long Twin, (6) 40W lamp | Electronic | 6 | 40 | 220 | 220
CFT40/6-LH | CFT40W | Compact Fluorescent, long Twin, (6) 40W lamp/ High Ballast Factor | Electronic | 6 | 40 | 233 | 233
CFT40/8-BX | CFT40W | Compact Fluorescent, Biax, (8) 40W lamp | Electronic | 8 | 40 | 288 | 288
CFT40/8-L | CFT40W | Compact Fluorescent, long Twin, (8) 40W lamp | Electronic | 8 | 40 | 300 | 300
CFT40/8-LH | CFT40W | Compact Fluorescent, long Twin, (8) 40W lamp/ High Ballast Factor | Electronic | 8 | 40 | 340 | 340
CFT40/9-BX | CFT40W | Compact Fluorescent, Biax, (9) 40W lamp | Electronic | 9 | 40 | 306 | 306
CFT5/1 | CFT5W | Compact Fluorescent, twin, (1) 5W lamp | Mag-STD | 1 | 5 | 9 | 9
CFT5/2 | CFT5W | Compact Fluorescent, twin, (2) 5W lamp | Mag-STD | 2 | 5 | 18 | 18
CFT50/12-BX | CFT50W | Compact Fluorescent, Biax, (12) 50W lamp | Electronic | 12 | 50 | 648 | 648
CFT50/1-BX | CFT50W | Compact Fluorescent, Biax, (1) 50W lamp | Electronic | 1 | 50 | 54 | 54
CFT50/2-BX | CFT50W | Compact Fluorescent, Biax, (2) 50W lamp | Electronic | 2 | 50 | 108 | 108
CFT50/3-BX | CFT50W | Compact Fluorescent, Biax, (3) 50W lamp | Electronic | 3 | 50 | 162 | 162
CFT50/4-BX | CFT50W | Compact Fluorescent, Biax, (4) 50W lamp | Electronic | 4 | 50 | 216 | 216
CFT50/5-BX | CFT50W | Compact Fluorescent, Biax, (5) 50W lamp | Electronic | 5 | 50 | 270 | 270
CFT50/6-BX | CFT50W | Compact Fluorescent, Biax, (6) 50W lamp | Electronic | 6 | 50 | 324 | 324
CFT50/8-BX | CFT50W | Compact Fluorescent, Biax, (8) 50W lamp | Electronic | 8 | 50 | 432 | 432
CFT50/9-BX | CFT50W | Compact Fluorescent, Biax, (9) 50W lamp | Electronic | 9 | 50 | 486 | 486
CFT55/12-BX | CFT55W | Compact Fluorescent, Biax, (12) 55W lamp | Electronic | 12 | 55 | 672 | 672
CFT55/1-BX | CFT55W | Compact Fluorescent, Biax, (1) 55W lamp | Electronic | 1 | 55 | 56 | 56
CFT55/2-BX | CFT55W | Compact Fluorescent, Biax, (2) 55W lamp | Electronic | 2 | 55 | 112 | 112
CFT55/3-BX | CFT55W | Compact Fluorescent, Biax, (3) 55W lamp | Electronic | 3 | 55 | 168 | 168
CFT55/4-BX | CFT55W | Compact Fluorescent, Biax, (4) 55W lamp | Electronic | 4 | 55 | 224 | 224
CFT55/5-BX | CFT55W | Compact Fluorescent, Biax, (5) 55W lamp | Electronic | 5 | 55 | 280 | 280
CFT55/6-BX | CFT55W | Compact Fluorescent, Biax, (6) 55W lamp | Electronic | 6 | 55 | 336 | 336
CFT55/6-L | CFT55W | Compact Fluorescent, long Twin, (6) 55W lamp | Electronic | 6 | 55 | 352 | 352
CFT55/6-LH | CFT55W | Compact Fluorescent, long Twin, (6) 55W lamp/ High Ballast Factor | Electronic | 6 | 55 | 373 | 373
CFT55/8-BX | CFT55W | Compact Fluorescent, Biax, (8) 55W lamp | Electronic | 8 | 55 | 448 | 448
CFT55/8-L | CFT55W | Compact Fluorescent, long Twin, (8) 55W lamp | Electronic | 8 | 55 | 468 | 468
CFT55/8-LH | CFT55W | Compact Fluorescent, long Twin, (8) 55W lamp/ High Ballast Factor | Electronic | 8 | 55 | 496 | 496
CFT55/9-BX | CFT55W | Compact Fluorescent, Biax, (9) 55W lamp | Electronic | 9 | 55 | 504 | 504
CFT7/1 | CFT7W | Compact Fluorescent, twin, (1) 7W lamp | Mag-STD | 1 | 7 | 10 | 10
CFT7/2 | CFT7W | Compact Fluorescent, twin, (2) 7W lamp | Mag-STD | 2 | 7 | 21 | 21
CFT9/1 | CFT9W | Compact Fluorescent, twin, (1) 9W lamp | Mag-STD | 1 | 9 | 11 | 11
CFT9/2 | CFT9W | Compact Fluorescent, twin, (2) 9W lamp | Mag-STD | 2 | 9 | 23 | 23
CFT9/3 | CFT9W | Compact Fluorescent, twin, (3) 9W lamp | Mag-STD | 3 | 9 | 34 | 34
Compact Fluorescent Lights (Screw-in)
CFC7/1 | CFC7 | Compact Fluorescent, Screw-in, (1) 7W lamp |  | 1 | 7 | 7 | 7
CFC9/1 | CFC9 | Compact Fluorescent, Screw-in, (1) 9W lamp |  | 1 | 9 | 9 | 9
CFC11/1 | CFC11 | Compact Fluorescent, Screw-in, (1) 11W lamp |  | 1 | 11 | 11 | 11
CFC13/1 | CFC13 | Compact Fluorescent, Screw-in, (1) 13W lamp |  | 1 | 13 | 13 | 13
CFC15/1 | CFC15 | Compact Fluorescent, Screw-in, (1) 15W lamp |  | 1 | 15 | 15 | 15
CFC18/1 | CFC18 | Compact Fluorescent, Screw-in, (1) 18W lamp |  | 1 | 18 | 18 | 18
CFC20/1 | CFC20 | Compact Fluorescent, Screw-in, (1) 20W lamp |  | 1 | 20 | 20 | 20
CFC23/1 | CFC23 | Compact Fluorescent, Screw-in, (1) 23W lamp |  | 1 | 23 | 23 | 23
CFC26/1 | CFC26 | Compact Fluorescent, Screw-in, (1) 26W lamp |  | 1 | 26 | 26 | 26
CFC30/1 | CFC30 | Compact Fluorescent, Screw-in, (1) 30W lamp |  | 1 | 30 | 30 | 30
EXIT Sign Fixtures
ECF5/1 | CFT5W | EXIT Compact Fluorescent, (1) 5W lamp | Mag-STD | 1 | 5 | 9 | 9
ECF5/2 | CFT5W | EXIT Compact Fluorescent, (2) 5W lamp | Mag-STD | 2 | 5 | 20 | 20
ECF7/1 | CFT7W | EXIT Compact Fluorescent, (1) 7W lamp | Mag-STD | 1 | 7 | 10 | 10
ECF7/2 | CFT7W | EXIT Compact Fluorescent, (2) 7W lamp | Mag-STD | 2 | 7 | 21 | 21
ECF8/1 | F8T5 | EXIT T5 Fluorescent, (1) 8W lamp | Mag-STD | 1 | 8 | 12 | 12
ECF8/2 | F8T5 | EXIT T5 Fluorescent, (2) 8W lamp | Mag-STD | 2 | 8 | 24 | 24
ECF9/1 | CFT9W | EXIT Compact Fluorescent, (1) 9W lamp | Mag-STD | 1 | 9 | 12 | 12
ECF9/2 | CFT9W | EXIT Compact Fluorescent, (2) 9W lamp | Mag-STD | 2 | 9 | 20 | 20
EI10/2 | I10 | EXIT Incandescent, (2) 10W lamp |  | 2 | 10 | 20 | 20
EI15/1 | I15 | EXIT Incandescent, (1) 15W lamp |  | 1 | 15 | 15 | 15
EI15/2 | I15 | EXIT Incandescent, (2) 15W lamp |  | 2 | 15 | 30 | 30
EI20/1 | I20 | EXIT Incandescent, (1) 20W lamp |  | 1 | 20 | 20 | 20
EI20/2 | I20 | EXIT Incandescent, (2) 20W lamp |  | 2 | 20 | 40 | 40
EI25/1 | I25 | EXIT Incandescent, (1) 25W lamp |  | 1 | 25 | 25 | 25
EI25/2 | I25 | EXIT Incandescent, (2) 25W lamp |  | 2 | 25 | 50 | 50
EI34/1 | I34 | EXIT Incandescent, (1) 34W lamp |  | 1 | 34 | 34 | 34
EI34/2 | I34 | EXIT Incandescent, (2) 34W lamp |  | 2 | 34 | 68 | 68
EI40/1 | I40 | EXIT Incandescent, (1) 40W lamp |  | 1 | 40 | 40 | 40
EI40/2 | I40 | EXIT Incandescent, (2) 40W lamp |  | 2 | 40 | 80 | 80
EI5/1 | I5 | EXIT Incandescent, (1) 5W lamp |  | 1 | 5 | 5 | 5
EI5/2 | I5 | EXIT Incandescent, (2) 5W lamp |  | 2 | 5 | 10 | 10
EI50/2 | I50 | EXIT Incandescent, (2) 50W lamp |  | 2 | 50 | 100 | 100
EI7.5/1 | I7.5 | EXIT Tungsten, (1) 7.5 W lamp |  | 1 | 7.5 | 8 | 8
EI7.5/2 | I7.5 | EXIT Tungsten, (2) 7.5 W lamp |  | 2 | 7.5 | 15 | 15
ELED0.5/1 | LED0.5W | EXIT Light Emitting Diode, (1) 0.5W lamp, Single Sided |  | 1 | 0.5 | 0.5 | 0.5
ELED0.5/2 | LED0.5W | EXIT Light Emitting Diode, (2) 0.5W lamp, Dual Sided |  | 2 | 0.5 | 1 | 1
ELED1.5/1 | LED1.5W | EXIT Light Emitting Diode, (1) 1.5W lamp, Single Sided |  | 1 | 1.5 | 1.5 | 1.5
ELED1.5/2 | LED1.5W | EXIT Light Emitting Diode, (2) 1.5W lamp, Dual Sided |  | 2 | 1.5 | 3 | 3
ELED10.5/1 | LED10.5W | EXIT Light Emitting Diode, (1) 10.5W lamp, Single Sided |  | 1 | 10.5 | 10.5 | 10.5
ELED10.5/2 | LED10.5W | EXIT Light Emitting Diode, (2) 10.5W lamp, Dual Sided |  | 2 | 10.5 | 21 | 21
ELED2/1 | LED2W | EXIT Light Emitting Diode, (1) 2W lamp, Single Sided |  | 1 | 2 | 2 | 2
ELED2/2 | LED2W | EXIT Light Emitting Diode, (2) 2W lamp, Dual Sided |  | 2 | 2 | 4 | 4
ELED3/1 | LED3W | EXIT Light Emitting Diode, (1) 3W lamp, Single Sided |  | 1 | 3 | 3 | 3
ELED3/2 | LED3W | EXIT Light Emitting Diode, (2) 3W lamp, Dual Sided |  | 2 | 3 | 6 | 6
ELED5/1 | LED5W | EXIT Light Emitting Diode, (1) 5W lamp, Single Sided |  | 1 | 5 | 5 | 5
ELED5/2 | LED5W | EXIT Light Emitting Diode, (2) 5W lamp, Dual Sided |  | 2 | 5 | 10 | 10
ELED8/1 | LED8W | EXIT Light Emitting Diode, (1) 8W lamp, Single Sided |  | 1 | 8 | 8 | 8
ELED8/2 | LED8W | EXIT Light Emitting Diode, (2) 8W lamp, Dual Sided |  | 2 | 8 | 16 | 16
Linear Fluorescent Fixtures
F1.51LS | F15T8 | Fluorescent, (1) 18" T8 lamp | Mag-STD | 1 | 15 | 19 | 19
F1.51SS | F15T12 | Fluorescent, (1) 18" T12 lamp | Mag-STD | 1 | 15 | 19 | 19
F1.52LS | F15T8 | Fluorescent, (2) 18" T8 lamp | Mag-STD | 2 | 15 | 36 | 36
F1.52SS | F15T12 | Fluorescent, (2) 18", T12 lamp | Mag-STD | 2 | 15 | 36 | 36
F21HS | F24T12/HO | Fluorescent, (1) 24", HO lamp | Mag-STD | 1 | 35 | 62 | 62
F21ILL | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 17 | 20 | 20
F21ILL/T2 | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 17 | 17 | 17
F21ILL/T2-R | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 2 Lamp Ballast | Electronic | 1 | 17 | 15 | 15
F21ILL/T3 | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 1 | 17 | 16 | 16
F21ILL/T3-R | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 3 Lamp Ballast | Electronic | 1 | 17 | 14 | 14
F21ILL/T4 | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 17 | 15 | 15
F21ILL/T4-R | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 4 Lamp Ballast | Electronic | 1 | 17 | 14 | 14
F21LL | F17T8 | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 17 | 16 | 16
F21LL/T2 | F17T8 | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 17 | 16 | 16
F21LL/T3 | F17T8 | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 1 | 17 | 17 | 17
F21LL/T4 | F17T8 | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 17 | 17 | 17
F21LL-R | F17T8 | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 1 | 17 | 15 | 15
F21LS | F17T8 | Fluorescent, (1) 24", T8 lamp, Standard Ballast | Mag-STD | 1 | 17 | 24 | 24
F21GL | F24T5 | Fluorescent, (1) 24", STD T5 lamp | Electronic | 1 | 14 | 18 | 18
F21SE | F20T12 | Fluorescent, (1) 24", STD lamp | Mag-ES | 1 | 20 | 26 | 26
F21SS | F20T12 | Fluorescent, (1) 24", STD lamp | Mag-STD | 1 | 20 | 28 | 28
F21GHL | F24T5/HO | Fluorescent, (1) 24", STD HO T5 lamp | Electronic | 1 | 24 | 29 | 29
F22SHS | F24T12/HO | Fluorescent, (2) 24", HO lamp | Mag-STD | 2 | 35 | 90 | 90
F22GHL | F24T5/HO | Fluorescent, (2) 24", STD HO T5 lamp | Electronic | 2 | 24 | 55 | 55
F22ILE | F17T8 | Fluorescent, (2) 24", T-8 Instant Start lamp, Energy Saving Magnetic Ballast | Mag-ES | 2 | 17 | 45 | 45
F22ILL | F17T8 | Fluorescent, (2) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 2 | 17 | 33 | 33
F22ILL/T4 | F17T8 | Fluorescent, (2) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 2 | 17 | 31 | 31
F22ILL/T4-R | F17T8 | Fluorescent, (2) 24", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 4 Lamp Ballast | Electronic | 2 | 17 | 28 | 28
F22ILL-R | F17T8 | Fluorescent, (2) 24", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 2 | 17 | 29 | 29
F22LL | F17T8 | Fluorescent, (2) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 2 | 17 | 31 | 31
F22LL/T4 | F17T8 | Fluorescent, (2) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 2 | 17 | 34 | 34
F22LL-R | F17T8 | Fluorescent, (2) 24", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 2 | 17 | 28 | 28
F22GL | F24T5 | Fluorescent, (2) 24", STD T5 lamp | Electronic | 2 | 14 | 35 | 35
F22SE | F20T12 | Fluorescent, (2) 24", STD lamp | Mag-ES | 2 | 20 | 51 | 51
F22SS | F20T12 | Fluorescent, (2) 24", STD lamp | Mag-STD | 2 | 20 | 56 | 56
F23ILL | F17T8 | Fluorescent, (3) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 3 | 17 | 47 | 47
F23ILL-H | F17T8 | Fluorescent, (3) 24", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 3 | 17 | 49 | 49
F23ILL-R | F17T8 | Fluorescent, (3) 24", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 3 | 17 | 43 | 43
F23LL | F17T8 | Fluorescent, (3) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 3 | 17 | 52 | 52
F23LL-R | F17T8 | Fluorescent, (3) 24", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 3 | 17 | 41 | 41
F23SE | F20T12 | Fluorescent, (3) 24", STD lamp | Mag-ES | 3 | 20 | 77 | 77
F23SS | F20T12 | Fluorescent, (3) 24", STD lamp | Mag-STD | 3 | 20 | 84 | 84
F24ILL | F17T8 | Fluorescent, (4) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 4 | 17 | 61 | 61
F24ILL-R | F17T8 | Fluorescent, (4) 24", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 4 | 17 | 55 | 55
F24LL | F17T8 | Fluorescent, (4) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 4 | 17 | 68 | 68
F24LL-R | F17T8 | Fluorescent, (4) 24", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 4 | 17 | 57 | 57
F24SE | F20T12 | Fluorescent, (4) 24", STD lamp | Mag-ES | 4 | 20 | 102 | 102
F24SS | F20T12 | Fluorescent, (4) 24", STD lamp | Mag-STD | 4 | 20 | 112 | 112
F26SE | F20T12 | Fluorescent, (6) 24", STD lamp | Mag-ES | 6 | 20 | 153 | 153
F26SS | F20T12 | Fluorescent, (6) 24", STD lamp | Mag-STD | 6 | 20 | 168 | 168
F31EE | F30T12/ES | Fluorescent, (1) 36", ES lamp | Mag-ES | 1 | 25 | 38 | 38
F31EE/T2 | F30T12/ES | Fluorescent, (1) 36", ES lamp, Tandem wired | Mag-ES | 1 | 25 | 33 | 33
F31EL | F30T12/ES | Fluorescent, (1) 36", ES lamp | Electronic | 1 | 25 | 26 | 26
F31ES | F30T12/ES | Fluorescent, (1) 36", ES lamp | Mag-STD | 1 | 25 | 42 | 42
F31ES/T2 | F30T12/ES | Fluorescent, (1) 36", ES lamp, Tandem wired | Mag-STD | 1 | 25 | 37 | 37
F31ILL | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 25 | 26 | 26
F31ILL/T2 | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 25 | 23 | 23
F31ILL/T2-H | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, HLO (BF: .96-1.1), Tandem 2 Lamp Ballast | Electronic | 1 | 25 | 24 | 24
F31ILL/T2-R | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, RLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 25 | 23 | 23
F31ILL/T3 | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 1 | 25 | 22 | 22
F31ILL/T3-R | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 3 Lamp Ballast | Electronic | 1 | 25 | 22 | 22
F31ILL/T4 | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 25 | 22 | 22
F31ILL/T4-R | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 4 Lamp Ballast | Electronic | 1 | 25 | 22 | 22
F31ILL-H | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 25 | 28 | 28
F31ILL-R | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 25 | 27 | 27
F31LL | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 25 | 24 | 24
F31LL/T2 | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 25 | 23 | 23
F31LL/T3 | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 1 | 25 | 24 | 24
F31LL/T4 | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 25 | 22 | 22
F31LL-H | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 25 | 26 | 26
F31LL-R | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 1 | 25 | 23 | 23
F31SE/T2 | F30T12 | Fluorescent, (1) 36", STD lamp, Tandem wired | Mag-ES | 1 | 30 | 37 | 37
F31GHL | F36T5/HO | Fluorescent, (1) 36", STD HO T5 lamp | Electronic | 1 | 39 | 43 | 43
F31SHS | F36T12/HO | Fluorescent, (1) 36", HO lamp | Mag-STD | 1 | 50 | 70 | 70
F31SL | F30T12 | Fluorescent, (1) 36", STD lamp | Electronic | 1 | 30 | 31 | 31
F31GL | F36T5 | Fluorescent, (1) 36", STD T5 lamp | Electronic | 1 | 21 | 27 | 27
F31SS | F30T12 | Fluorescent, (1) 36", STD lamp | Mag-STD | 1 | 30 | 46 | 46
F31SS/T2 | F30T12 | Fluorescent, (1) 36", STD lamp, Tandem wired | Mag-STD | 1 | 30 | 41 | 41
F32EE | F30T12/ES | Fluorescent, (2) 36", ES lamp | Mag-ES | 2 | 25 | 66 | 66
F32EL | F30T12/ES | Fluorescent, (2) 36", ES lamp | Electronic | 2 | 25 | 50 | 50
F32ES | F30T12/ES | Fluorescent, (2) 36", ES lamp | Mag-STD | 2 | 25 | 73 | 73
F32ILL | F25T8 | Fluorescent, (2) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 2 | 25 | 46 | 46
F32ILL/T4 | F25T8 | Fluorescent, (2) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 2 | 25 | 44 | 44
F32ILL/T4-R | F25T8 | Fluorescent, (2) 36", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 4 Lamp Ballast | Electronic | 2 | 25 | 43 | 43
F32ILL-H | F25T8 | Fluorescent, (2) 36", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 2 | 25 | 48 | 48
F32ILL-R | F25T8 | Fluorescent, (2) 36", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 2 | 25 | 46 | 46
F32LE | F25T8 | Fluorescent, (2) 36", T-8 lamp | Mag-ES | 2 | 25 | 65 | 65
F32LL | F25T8 | Fluorescent, (2) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 2 | 25 | 46 | 46
F32LL/T4 | F25T8 | Fluorescent, (2) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 2 | 25 | 45 | 45
F32LL-H | F25T8 | Fluorescent, (2) 36", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1) | Electronic | 2 | 25 | 50 | 50
F32LL-R | F25T8 | Fluorescent, (2) 36", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 2 | 25 | 42 | 42
F32LL-V | F25T8 | Fluorescent, (2) 36", T-8 lamp, Rapid Start Ballast, VHLO (BF>1.1) | Electronic | 2 | 25 | 70 | 70
F32SE | F30T12 | Fluorescent, (2) 36", STD lamp | Mag-ES | 2 | 30 | 74 | 74
F32GHL | F36T5/HO | Fluorescent, (2) 36", STD HO T5 lamp | Electronic | 2 | 39 | 85 | 85
F32SHS | F36T12/HO | Fluorescent, (2) 36", HO, lamp | Mag-STD | 2 | 50 | 114 | 114
F32SL | F30T12 | Fluorescent, (2) 36", STD lamp | Electronic | 2 | 30 | 58 | 58
F32GL | F36T5 | Fluorescent, (1) 36", STD T5 lamp | Electronic | 2 | 21 | 52 | 52
F32SS | F30T12 | Fluorescent, (2) 36", STD lamp | Mag-STD | 2 | 30 | 81 | 81
F33EE | F30T12/ES | Fluorescent, (3) 36", ES lamp | Mag-ES | 3 | 25 | 104 | 104
F33EL | F30T12/ES | Fluorescent, (3) 36", ES lamp | Electronic | 3 | 25 | 76 | 76
F33ES | F30T12/ES | Fluorescent, (3) 36", ES lamp | Mag-STD | 3 | 25 | 115 | 115
F33ILL | F25T8 | Fluorescent, (3) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 3 | 25 | 67 | 67
F33ILL-R | F25T8 | Fluorescent, (3) 36", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 3 | 25 | 66 | 66
F33LL | F25T8 | Fluorescent, (3) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 3 | 25 | 72 | 72
F33LL-R | F25T8 | Fluorescent, (3) 36", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 3 | 25 | 62 | 62
F33SE | F30T12 | Fluorescent, (3) 36", STD lamp, (1) STD ballast and (1) ES ballast | Mag-ES | 3 | 30 | 120 | 120
F33SS | F30T12 | Fluorescent, (3) 36", STD lamp | Mag-STD | 3 | 30 | 127 | 127
F34EE | F30T12/ES | Fluorescent, (4) 36", ES lamp | Mag-ES | 4 | 25 | 132 | 132
F34EL | F30T12/ES | Fluorescent, (4) 36", ES lamp | Electronic | 4 | 25 | 100 | 100
F34ILL | F25T8 | Fluorescent, (4) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 4 | 25 | 87 | 87
F34ILL-R | F25T8 | Fluorescent, (4) 36", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 4 | 25 | 86 | 86
F34LL | F25T8 | Fluorescent, (4) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 4 | 25 | 89 | 89
F34LL-R | F25T8 | Fluorescent, (4) 36", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 4 | 25 | 84 | 84
F34SE | F30T12 | Fluorescent, (4) 36", STD lamp | Mag-ES | 4 | 30 | 148 | 148
F34SL | F30T12 | Fluorescent, (4) 36", STD lamp | Electronic | 4 | 30 | 116 | 116
F34SS | F30T12 | Fluorescent, (4) 36", STD lamp | Mag-STD | 4 | 30 | 162 | 162
F36EE | F30T12/ES | Fluorescent, (6) 36", ES lamp | Mag-ES | 6 | 25 | 198 | 198
F36ILL-R | F25T8 | Fluorescent, (6) 36", T-8 lamp, Instant Start Ballast, RLO (BF<.85) | Electronic | 6 | 25 | 134 | 134
F36SE | F30T12 | Fluorescent, (6) 36", STD lamp | Mag-ES | 6 | 30 | 238 | 238
F40EE/D1 | None | Fluorescent, (0) 48" lamp, Completely delamped fixture with (1) hot ballast | Mag-ES | 0 | 0 | 4 | 4
F40EE/D2 | None | Fluorescent, (0) 48" lamp, Completely delamped fixture with (2) hot ballast | Mag-ES | 0 | 0 | 8 | 8
F41EE | F40T12/ES | Fluorescent, (1) 48", ES lamp | Mag-ES | 1 | 34 | 43 | 43
F41EE/D2 | F40T12/ES | Fluorescent, (1) 48", ES lamp, 2 ballast | Mag-ES | 1 | 34 | 43 | 43
F41EE/T2 | F40T12/ES | Fluorescent, (1) 48", ES lamp, tandem wired, 2-lamp ballast | Mag-ES | 1 | 34 | 36 | 36
F41EHS | F48T12/HO/ES | Fluorescent, (1) 48", ES HO lamp | Mag-STD | 1 | 55 | 80 | 80
F41EIS | F48T12/ES | Fluorescent, (1) 48" ES Instant Start lamp. Magnetic ballast | Mag-STD | 1 | 30 | 51 | 51
F41EL | F40T12/ES | Fluorescent, (1) 48", T12 ES lamp, Electronic Ballast | Electronic | 1 | 34 | 32 | 32
F41EL/T2 | F40T12/ES | Fluorescent, (1) 48", T-12 ES lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 34 | 32 | 32
F41ES | F40T12/ES | Fluorescent, (1) 48", ES lamp | Mag-STD | 1 | 34 | 50 | 50
F41EVS | F48T12/VHO/ES | Fluorescent, (1) 48", VHO ES lamp | Mag-STD | 1 |  | 123 | 123
F41IAL | F25T12 | Fluorescent, (1) 48", F25T12 lamp, Instant Start Ballast | Electronic | 1 | 25 | 25 | 25
F41IAL/T2-R | F25T12 | Fluorescent, (1) 48", F25T12 lamp, Instant Start, Tandem 2-Lamp Ballast, RLO (BF<0.85) | Electronic | 1 | 25 | 19 | 19
F41IAL/T3-R | F25T12 | Fluorescent, (1) 48", F25T12 lamp, Instant Start, Tandem 3-Lamp Ballast, RLO (BF<0.85) | Electronic | 1 | 25 | 20 | 20
F41ILL | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 32 | 31 | 31
F41SILL | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 30 | 28 | 28
F41SILL/T2 | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 30 | 27 | 27
F41SILL/T3 | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 1 | 30 | 27 | 27
F41SILL/T4 | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 30 | 26 | 26
F41SILL-R | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 30 | 25 | 25
F41SILL/T2-R | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 2 Lamp Ballast | Electronic | 1 | 30 | 24 | 24
F41SILL/T3-R | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 3 Lamp Ballast | Electronic | 1 | 30 | 24 | 24
F41SILL/T4-R | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 1 | 30 | 23 | 23
F41SILL-H | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 30 | 37 | 37
F41SILL/T2-H | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1), Tandem 2 Lamp Ballast | Electronic | 1 | 30 | 36 | 36
F41SILL/T3-H | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1), Tandem 3 Lamp Ballast | Electronic | 1 | 30 | 36 | 36
F41SSILL | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 28 | 26 | 26
F41SSILL/T2 | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 28 | 25 | 25
F41SSILL/T3 | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 1 | 28 | 25 | 25
F41SSILL/T4 | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 28 | 24 | 24
F41SSILL-R | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 28 | 23 | 23
F41SSILL/T2-R | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 2 Lamp Ballast | Electronic | 1 | 28 | 22 | 22
F41SSILL/T3-R | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 3 Lamp Ballast | Electronic | 1 | 28 | 22 | 22
F41SSILL/T4-R | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 1 | 28 | 21 | 21
F41SSILL-H | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 28 | 33 | 33
F41SSILL/T2-H | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1), Tandem 2 Lamp Ballast | Electronic | 1 | 28 | 32 | 32
F41SSILL/T3-H | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1), Tandem 3 Lamp Ballast | Electronic | 1 | 28 | 32 | 32
F41ILL/T2 | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 32 | 30 | 30
F41ILL/T2-H | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1), Tandem 2 Lamp Ballast | Electronic | 1 | 32 | 33 | 33
F41ILL/T2-R | F32T8 | Fluorescent, (1) 48", T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 2 Lamp Ballast | Electronic | 1 | 32 | 26 | 26
F41ILL/T3 | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 1 | 32 | 30 | 30
F41ILL/T3-H | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1), Tandem 3 Lamp Ballast | Electronic | 1 | 32 | 31 | 31
F41ILL/T3-R | F32T8 | Fluorescent, (1) 48", T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 3 Lamp Ballast | Electronic | 1 | 32 | 26 | 26
F41ILL/T4 | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 32 | 28 | 28
F41ILL/T4-R | F32T8 | Fluorescent, (1) 48", T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 1 | 32 | 26 | 26
F41ILL-H | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 32 | 36 | 36
F41LE | F32T8 | Fluorescent, (1) 48", T-8 lamp | Mag-ES | 1 | 32 | 35 | 35
F41LL | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 32 | 32 | 32
F41LL/T2 | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 32 | 30 | 30
F41LL/T2-H | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1), Tandem 2 Lamp Ballast | Electronic | 1 | 32 | 39 | 39
F41LL/T2-R | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85), Tandem 2 Lamp Ballast | Electronic | 1 | 32 | 27 | 27
F41LL/T3 | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 1 | 32 | 31 | 31
F41LL/T3-H | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1), Tandem 3 Lamp Ballast | Electronic | 1 | 32 | 33 | 33
F41LL/T3-R | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85), Tandem 3 Lamp Ballast | Electronic | 1 | 32 | 25 | 25
F41LL/T4 | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 32 | 30 | 30
F41LL/T4-R | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 1 | 32 | 26 | 26
F41LL-H | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 32 | 39 | 39
F41LL-R | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 1 | 32 | 27 | 27
F41SE | F40T12 | Fluorescent, (1) 48", STD lamp | Mag-ES | 1 | 40 | 50 | 50
F41GHL | F48T5/HO | Fluorescent, (1) 48", STD HO T5 lamp | Electronic | 1 | 54 | 59 | 59
F41SHS | F48T12/HO | Fluorescent, (1) 48", STD HO lamp | Mag-STD | 1 | 60 | 85 | 85
F41SIL | F48T12 | Fluorescent, (1) 48", STD IS lamp, Electronic ballast | Electronic | 1 | 39 | 46 | 46
F41SIL/T2 | F48T12 | Fluorescent, (1) 48", STD IS lamp, Electronic ballast, tandem wired | Electronic | 1 | 39 | 37 | 37
F41SIS | F48T12 | Fluorescent, (1) 48", STD IS lamp | Mag-STD | 1 | 39 | 60 | 60
F41SIS/T2 | F48T12 | Fluorescent, (1) 48", STD IS lamp, tandem to 2-lamp ballast | Mag-STD | 1 | 39 | 52 | 52
F41GL | F48T5 | Fluorescent, (1) 48", STD T5 lamp | Electronic | 1 | 28 | 32 | 32
F41SL/T2 | F40T12 | Fluorescent, (1) 48", T-12 STD lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 40 | 36 | 36
F41SS | F40T12 | Fluorescent, (1) 48", STD lamp | Mag-STD | 1 | 40 | 57 | 57
F41SVS | F48T12/VHO | Fluorescent, (1) 48", STD VHO lamp | Mag-STD | 1 | 110 | 135 | 135
F41TS | F40T10 | Fluorescent, (1) 48", T-10 lamp | Mag-STD | 1 | 40 | 51 | 51
F42EE | F40T12/ES | Fluorescent, (2) 48", ES lamp | Mag-ES | 2 | 34 | 72 | 72
F42EE/D2 | F40T12/ES | Fluorescent, (2) 48", ES lamp, 2 Ballasts (delamped) | Mag-ES | 2 | 34 | 76 | 76
F42EHS | F48T12/HO/ES | Fluorescent, (2) 42", HO lamp (3.5' lamp) | Mag-STD | 2 | 55 | 135 | 135
F42EIS | F48T12/ES | Fluorescent, (2) 48" ES Instant Start lamp. Magnetic ballast | Mag-STD | 2 | 30 | 82 | 82
F42EL | F40T12/ES | Fluorescent, (2) 48", T12 ES lamps, Electronic Ballast | Electronic | 2 | 34 | 60 | 60
F42ES | F40T12/ES | Fluorescent, (2) 48", ES lamp | Mag-STD | 2 | 34 | 80 | 80
F42EVS | F48T12/VHO/ES | Fluorescent, (2) 48", VHO ES lamp | Mag-STD | 2 |  | 210 | 210
F42IAL/T4-R | F25T12 | Fluorescent, (2) 48", F25T12 lamp, Instant Start, Tandem 4-Lamp Ballast, RLO (BF<0.85) | Electronic | 2 | 25 | 40 | 40
F42IAL-R | F25T12 | Fluorescent, (2) 48", F25T12 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 2 | 25 | 39 | 39
F42ILL | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 2 | 32 | 59 | 59
F42SILL | F30T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 2 | 30 | 53 | 53
F42SILL/T4 | F30T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 2 | 30 | 52 | 52
F42SILL-R | F30T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 2 | 30 | 47 | 47
F42SILL/T4-R | F30T8 | Fluorescent, (2) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 2 | 30 | 46 | 46
F42SILL-H | F30T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-2.2) | Electronic | 2 | 30 | 72 | 72
F42SSILL | F28T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 2 | 28 | 48 | 48
F42SSILL/T4 | F28T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 2 | 28 | 47 | 47
F42SSILL-R | F28T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 2 | 28 | 45 | 45
F42SSILL/T4-R | F28T8 | Fluorescent, (2) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 2 | 28 | 44 | 44
F42SSILL-H | F28T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-2.2) | Electronic | 2 | 28 | 67 | 67
F42ILL/T4 | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 2 | 32 | 56 | 56
F42ILL/T4-R | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 2 | 32 | 51 | 51
F42ILL-H | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 2 | 32 | 65 | 65
F42ILL-R | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 2 | 32 | 52 | 52
F42ILL-V | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, VHLO (BF>1.1) | Electronic | 2 | 32 | 79 | 79
F42LE | F32T8 | Fluorescent, (2) 48", T-8 lamp | Mag-ES | 2 | 32 | 71 | 71
F42LL | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 2 | 32 | 60 | 60
F42LL/T4 | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 2 | 32 | 59 | 59
F42LL/T4-R | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 2 | 32 | 53 | 53
F42LL-H | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1) | Electronic | 2 | 32 | 70 | 70
F42LL-R | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 2 | 32 | 54 | 54
F42LL-V | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, VHLO (BF>1.1) | Electronic | 2 | 32 | 85 | 85
F42SE | F40T12 | Fluorescent, (2) 48", STD lamp | Mag-ES | 2 | 40 | 86 | 86
F42GHL | F48T5/HO | Fluorescent, (2) 48", STD HO T5 lamp | Electronic | 2 | 54 | 117 | 117
F42SHS | F48T12/HO | Fluorescent, (2) 48", STD HO lamp | Mag-STD | 2 | 60 | 145 | 145
F42SIL | F48T12 | Fluorescent, (2) 48", STD IS lamp, Electronic ballast | Electronic | 2 | 39 | 74 | 74
F42SIS | F48T12 | Fluorescent, (2) 48", STD IS lamp | Mag-STD | 2 | 39 | 103 | 103
F42GL | F48T5 | Fluorescent, (2) 48", STD T5 lamp | Electronic | 2 | 28 | 63 | 63
F42SS | F40T12 | Fluorescent, (2) 48", STD lamp | Mag-STD | 2 | 40 | 94 | 94
F42SVS | F48T12/VHO | Fluorescent, (2) 48", STD VHO lamp | Mag-STD | 2 | 110 | 242 | 242
F43EE | F40T12/ES | Fluorescent, (3) 48", ES lamp | Mag-ES | 3 | 34 | 115 | 115
F43EHS | F48T12/HO/ES | Fluorescent, (3) 48", ES HO lamp (3.5' lamp) | Mag-STD | 3 | 55 | 215 | 215
F43EIS | F48T12/ES | Fluorescent, (3) 48" ES Instant Start lamp. Magnetic ballast | Mag-STD | 3 | 30 | 133 | 133
F43EL | F40T12/ES | Fluorescent, (3) 48", T12 ES lamps, Electronic Ballast | Electronic | 3 | 34 | 92 | 92
F43ES | F40T12/ES | Fluorescent, (3) 48", ES lamp | Mag-STD | 3 | 34 | 130 | 130
F43EVS | F48T12/VHO/ES | Fluorescent, (3) 48", VHO ES lamp | Mag-STD | 3 |  | 333 | 333
F43IAL-R | F25T12 | Fluorescent, (3) 48", F25T12 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 3 | 25 | 60 | 60
F43ILL | F32T8 | Fluorescent, (3) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 3 | 32 | 89 | 89
F43SILL | F30T8 | Fluorescent, (3) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 3 | 30 | 78 | 78
F43SILL-R | F30T8 | Fluorescent, (3) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 3 | 30 | 70 | 70
F43SILL-H | F30T8 | Fluorescent, (3) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-3.3) | Electronic | 3 | 30 | 105 | 105
F43SSILL | F28T8 | Fluorescent, (3) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 3 | 28 | 72 | 72
F43SSILL-R | F28T8 | Fluorescent, (3) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 3 | 28 | 66 | 66
F43SSILL-H | F28T8 | Fluorescent, (3) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-3.3) | Electronic | 3 | 28 | 98 | 98
F43ILL/2 | F32T8 | Fluorescent, (3) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), (2) ballast | Electronic | 3 | 32 | 90 | 90
F43ILL-H | F32T8 | Fluorescent, (3) 48", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 3 | 32 | 93 | 93
F43ILL-R | F32T8 | Fluorescent, (3) 48", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 3 | 32 | 78 | 78
F43ILL-V | F32T8 | Fluorescent, (3) 48", T-8 lamp, Instant Start Ballast, VHLO (BF>1.1) | Electronic | 3 | 32 | 112 | 112
F43LE | F32T8 | Fluorescent, (3) 48", T-8 lamp | Mag-ES | 3 | 32 | 110 | 110
F43LL | F32T8 | Fluorescent, (3) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 3 | 32 | 93 | 93
F43LL/2 | F32T8 | Fluorescent, (3) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), (2) ballast | Electronic | 3 | 32 | 92 | 92
F43LL-H | F32T8 | Fluorescent, (3) 48", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1) | Electronic | 3 | 32 | 98 | 98
F43LL-R | F32T8 | Fluorescent, (3) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 3 | 32 | 76 | 76
F43SE | F40T12 | Fluorescent, (3) 48", STD lamp | Mag-ES | 3 | 40 | 136 | 136
F43GHL | F48T5/HO | Fluorescent, (3) 48", STD HO T5 lamp | Electronic | 3 | 54 | 177 | 177
F43SHS | F48T12/HO | Fluorescent, (3) 48", STD HO lamp | Mag-STD | 3 | 60 | 230 | 230
F43SIL | F40T12 | Fluorescent, (3) 48", STD IS lamp, Electronic ballast | Electronic | 3 | 39 | 120 | 120
F43SIS | F48T12 | Fluorescent, (3) 48", STD IS lamp | Mag-STD | 3 | 39 | 162 | 162
F43SS | F40T12 | Fluorescent, (3) 48", STD lamp | Mag-STD | 3 | 40 | 151 | 151
F43SVS | F48T12/VHO | Fluorescent, (3) 48", STD VHO lamp | Mag-STD | 3 | 110 | 377 | 377
F44EE | F40T12/ES | Fluorescent, (4) 48", ES lamp | Mag-ES | 4 | 34 | 144 | 144
F44EE/D4 | F40T12/ES | Fluorescent, (4) 48", ES lamp, 4 Ballasts (delamped) | Mag-ES | 4 | 34 | 152 | 152
F44EHS | F48T12/HO/ES | Fluorescent, (4) 48", ES HO lamp | Mag-STD | 4 | 55 | 270 | 270
F44EIS | F48T12/ES | Fluorescent, (4) 48" ES Instant Start lamp, Magnetic ballast | Mag-STD | 4 | 30 | 164 | 164
F44EL | F40T12/ES | Fluorescent, (4) 48", T12 ES lamp, Electronic Ballast | Electronic | 4 | 34 | 120 | 120
F44ES | F40T12/ES | Fluorescent, (4) 48", ES lamp | Mag-STD | 4 | 34 | 160 | 160
F44EVS | F48T12/VHO/ES | Fluorescent, (4) 48", VHO ES lamp | Mag-STD | 4 |  | 420 | 420
F44IAL-R | F25T12 | Fluorescent, (4) 48", F25T12 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 4 | 25 | 80 | 80
F44ILL | F32T8 | Fluorescent, (4) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 4 | 32 | 112 | 112
F44SILL | F30T8 | Fluorescent, (4) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 4 | 30 | 105 | 105
F44SILL-R | F30T8 | Fluorescent, (4) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 4 | 30 | 91 | 91
F44SILL-H | F30T8 | Fluorescent, (4) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-4.4) | Electronic | 4 | 30 | 140 | 140
F44SSILL | F28T8 | Fluorescent, (4) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 4 | 28 | 96 | 96
F44SSILL-R | F28T8 | Fluorescent, (4) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 4 | 28 | 86 | 86
F44SSILL-H | F28T8 | Fluorescent, (4) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-4.4) | Electronic | 4 | 28 | 131 | 131
F44ILL/2 | F32T8 | Fluorescent, (4) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), (2) ballast | Electronic | 4 | 32 | 118 | 118
F44ILL-R | F32T8 | Fluorescent, (4) 48", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 4 | 32 | 102 | 102
F44LE | F32T8 | Fluorescent, (4) 48", T-8 lamp | Mag-ES | 4 | 32 | 142 | 142
F44LL | F32T8 | Fluorescent, (4) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 4 | 32 | 118 | 118
F44LL/2 | F32T8 | Fluorescent, (4) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), (2) ballast | Electronic | 4 | 32 | 120 | 120
F44LL-R | F32T8 | Fluorescent, (4) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 4 | 32 | 105 | 105
F44SE | F40T12 | Fluorescent, (4) 48", STD lamp | Mag-ES | 4 | 40 | 172 | 172
F44GHL | F48T5/HO | Fluorescent, (4) 48", STD HO T5 lamp | Electronic | 4 | 54 | 234 | 234
F44SHS | F48T12/HO | Fluorescent, (4) 48", STD HO lamp | Mag-STD | 4 | 60 | 290 | 290
F44SIL | F48T12 | Fluorescent, (4) 48", STD IS lamp, Electronic ballast | Electronic | 4 | 39 | 148 | 148
F44SIS | F48T12 | Fluorescent, (4) 48", STD IS lamp | Mag-STD | 4 | 39 | 204 | 204
F44SS | F40T12 | Fluorescent, (4) 48", STD lamp | Mag-STD | 4 | 40 | 188 | 188
F44SVS | F48T12/VHO | Fluorescent, (4) 48", STD VHO lamp | Mag-STD | 4 | 110 | 484 | 484
F45ILL | F32T8 | Fluorescent, (5) 48", T-8 lamp, (1) 3-lamp IS ballast and (1) 2-lamp IS ballast, NLO (BF: .85-.95) | Electronic | 5 | 32 | 148 | 148
F45GHL | F48T5/HO | Fluorescent, (5) 48", STD HO T5 lamp | Electronic | 5 | 54 | 294 | 294
F46EE | F40T12/ES | Fluorescent, (6) 48", ES lamp | Mag-ES | 6 | 34 | 216 | 216
F46EL | F40T12/ES | Fluorescent, (6) 48", ES lamp | Electronic | 6 | 34 | 186 | 186
F46ES | F40T12/ES | Fluorescent, (6) 48", ES lamp | Mag-STD | 6 | 34 | 236 | 236
F46EHS | F48T12/HO/ES | Fluorescent, (6) 48", ES HO lamp (3.5' lamp) | Mag-STD | 6 | 55 | 405 | 405
F46ILL | F32T8 | Fluorescent, (6) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 6 | 32 | 175 | 175
F46ILL-R | F32T8 | Fluorescent, (6) 48", T-8 lamp, Instant Start Ballast, RLO (BF< .85) | Electronic | 6 | 32 | 156 | 156
F46LL | F32T8 | Fluorescent, (6) 48", T-8 lamp, NLO (BF: .85-.95) | Electronic | 6 | 32 | 182 | 182
F46GHL | F48T5/HO | Fluorescent, (6) 48", STD HO T5 lamp | Electronic | 6 | 54 | 351 | 351
F46SE | F40T12 | Fluorescent, (6) 48", STD lamp | Mag-ES | 6 | 40 | 258 | 258
F46SS | F40T12 | Fluorescent, (6) 48", STD lamp | Mag-STD | 6 | 40 | 282 | 282
F48EE | F40T12/ES | Fluorescent, (8) 48", ES lamp | Mag-ES | 8 | 34 | 288 | 288
F48EHS | F48T12/HO/ES | Fluorescent, (8) 48", ES HO lamp (3.5' lamp) | Mag-STD | 8 | 55 | 540 | 540
F48ILL | F32T8 | Fluorescent, (8) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 8 | 32 | 224 | 224
F48ILL-R | F32T8 | Fluorescent, (8) 48", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 8 | 32 | 204 | 204
F48GHL | F48T5/HO | Fluorescent, (8) 48", STD HO T5 lamp | Electronic | 8 | 54 | 468 | 468
F51ILHL | F60T12/HO | Fluorescent, (1) 60", T-8 HO lamp, Instant Start Ballast | Electronic | 1 | 55 | 59 | 59
F51ILL | F40T8 | Fluorescent, (1) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 40 | 36 | 36
F51ILL/T2 | F40T8 | Fluorescent, (1) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 40 | 36 | 36
F51ILL/T3 | F40T8 | Fluorescent, (1) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 1 | 40 | 35 | 35
F51ILL/T4 | F40T8 | Fluorescent, (1) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 40 | 34 | 34
F51ILL-R | F40T8 | Fluorescent, (1) 60", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 40 | 43 | 43
F51SHE | F60T12/HO | Fluorescent, (1) 60", STD HO lamp | Mag-ES | 1 | 75 | 88 | 88
F51SHL | F60T12/HO | Fluorescent, (1) 60", STD HO lamp | Electronic | 1 | 75 | 69 | 69
F51GHL | F60T5/HO | Fluorescent, (1) 60", STD HO T5 lamp | Electronic | 1 | 80 | 89 | 89
F51SHS | F60T12/HO | Fluorescent, (1) 60", STD HO lamp | Mag-STD | 1 | 75 | 92 | 92
F51SL | F60T12 | Fluorescent, (1) 60", STD lamp | Electronic | 1 | 50 | 44 | 44
F51GL | F60T5 | Fluorescent, (1) 60", STD T5 lamp | Electronic | 1 | 35 | 39 | 39
F51SS | F60T12 | Fluorescent, (1) 60", STD lamp | Mag-STD | 1 | 50 | 63 | 63
F51SVS | F60T12/VHO | Fluorescent, (1) 60", VHO ES lamp | Mag-STD | 1 | 135 | 165 | 165
F52ILHL | F60T12/HO | Fluorescent, (2) 60", T-8 HO lamp, Instant Start Ballast | Electronic | 2 | 55 | 123 | 123
F52ILL | F40T8 | Fluorescent, (2) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 2 | 40 | 72 | 72
F52ILL/T4 | F40T8 | Fluorescent, (2) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 2 | 40 | 67 | 67
F52ILL-H | F40T8 | Fluorescent, (2) 60", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 2 | 40 | 80 | 80
F52ILL-R | F40T8 | Fluorescent, (2) 60", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 2 | 40 | 73 | 73
F52SHE | F60T12/HO | Fluorescent, (2) 60", STD HO lamp | Mag-ES | 2 | 75 | 176 | 176
F52SHL | F60T12/HO | Fluorescent, (2) 60", STD HO lamp | Electronic | 2 | 75 | 138 | 138
F52SHS | F60T12/HO | Fluorescent, (2) 60", STD HO lamp | Mag-STD | 2 | 75 | 168 | 168
F52SL | F60T12 | Fluorescent, (2) 60", STD lamp | Electronic | 2 | 50 | 88 | 88
F52GL | F60T5 | Fluorescent, (2) 60", STD T5 lamp | Electronic | 2 | 35 | 76 | 76
F52SS | F60T12 | Fluorescent, (2) 60", STD lamp | Mag-STD | 2 | 50 | 128 | 128
F52SVS | F60T12/VHO | Fluorescent, (2) 60", VHO ES lamp | Mag-STD | 2 | 135 | 310 | 310
F53ILL | F40T8 | Fluorescent, (3) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 3 | 40 | 106 | 106
F53ILL-H | F40T8 | Fluorescent, (3) 60", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 3 | 40 | 108 | 108
F54ILL | F40T8 | Fluorescent, (4) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 4 | 40 | 134 | 134
F54ILL-H | F40T8 | Fluorescent, (4) 60", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 4 | 40 | 126 | 126
F61ISL | F72T12 | Fluorescent, (1) 72", STD lamp, IS electronic ballast | Electronic | 1 | 55 | 68 | 68
F61SE | F72T12 | Fluorescent, (1) 72", STD lamp | Mag-ES | 1 | 55 | 76 | 76
F61SHS | F72T12/HO | Fluorescent, (1) 72", STD HO lamp | Mag-STD | 1 | 85 | 120 | 120
F61SS | F72T12 | Fluorescent, (1) 72", STD lamp | Mag-STD | 1 | 55 | 90 | 90
F61SVS | F72T12/VHO | Fluorescent, (1) 72", VHO lamp | Mag-STD | 1 | 160 | 180 | 180
F62ILHL | F72T8 | Fluorescent, (2) 72", T-8 HO lamp, Instant Start Ballast | Electronic | 2 | 65 | 147 | 147
F62ISL | F72T12 | Fluorescent, (2) 72", STD lamp, IS electronic ballast | Electronic | 2 | 55 | 108 | 108
F62SE | F72T12 | Fluorescent, (2) 72", STD lamp | Mag-ES | 2 | 55 | 122 | 122
F62SHE | F72T12/HO | Fluorescent, (2) 72", STD HO lamp | Mag-ES | 2 | 85 | 194 | 194
F62SHS | F72T12/HO | Fluorescent, (2) 72", STD HO lamp | Mag-STD | 2 | 85 | 220 | 220
F62SL | F72T12 | Fluorescent, (2) 72", STD lamp | Electronic | 2 | 55 | 108 | 108
F62SS | F72T12 | Fluorescent, (2) 72", STD lamp | Mag-STD | 2 | 55 | 145 | 145
F62SVS | F72T12/VHO | Fluorescent, (2) 72", VHO lamp | Mag-STD | 2 | 160 | 330 | 330
F63ISL | F72T12 | Fluorescent, (3) 72", STD lamp, IS electronic ballast | Electronic | 3 | 55 | 176 | 176
F63SS | F72T12 | Fluorescent, (3) 72", STD lamp | Mag-STD | 3 | 55 | 202 | 202
F64ISL | F72T12 | Fluorescent, (4) 72", STD lamp, IS electronic ballast | Electronic | 4 | 55 | 216 | 216
F64SE | F72T12 | Fluorescent, (4) 72", STD lamp | Mag-ES | 4 | 55 | 230 | 230
F64SHE | F72T12/HO | Fluorescent, (4) 72", STD HO lamp | Mag-ES | 4 | 85 | 388 | 388
F64SS | F72T12 | Fluorescent, (4) 72", STD lamp | Mag-STD | 4 | 55 | 244 | 244
F81EE | F96T12/ES | Fluorescent, (1) 96", ES lamp | Mag-ES | 1 | 60 | 61 | 61
F81EE/T2 | F96T12/ES | Fluorescent, (1) 96", ES lamp, tandem to 2-lamp ballast | Mag-ES | 1 | 60 | 62 | 62
F81EHL | F96T12/HO/ES | Fluorescent, (1) 96", ES HO lamp | Electronic | 1 | 95 | 80 | 80
F81EHL/T2 | F96T12/HO/ES | Fluorescent, (1) 96", ES HO lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 95 | 85 | 85
F81EHS | F96T12/HO/ES | Fluorescent, (1) 96", ES HO lamp | Mag-STD | 1 | 95 | 125 | 125
F81EL | F96T12/ES | Fluorescent, (1) 96", ES lamp | Electronic | 1 | 60 | 60 | 60
F81EL/T2 | F96T12/ES | Fluorescent, (1) 96", ES lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 60 | 55 | 55
F81ES | F96T12/ES | Fluorescent, (1) 96", ES lamp | Mag-STD | 1 | 60 | 83 | 83
F81ES/T2 | F96T12/ES | Fluorescent, (1) 96", ES lamp, tandem to 2-lamp ballast | Mag-STD | 1 | 60 | 64 | 64
F81EVS | F96T12/VHO/ES | Fluorescent, (1) 96", ES VHO lamp | Mag-STD | 1 | 185 | 200 | 200
F81ILL | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 59 | 58 | 58
F81ILL/T2 | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 59 | 55 | 55
F81ILL/T2-R | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 2 Lamp Ballast | Electronic | 1 | 59 | 49 | 49
F81ILL-H | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 59 | 68 | 68
F81ILL-R | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 59 | 57 | 57
F81ILL-V | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, VHLO (BF>1.1) | Electronic | 1 | 59 | 71 | 71
F81LHL | F96T8/HO | Fluorescent, (1) 96", T8 HO lamp | Electronic | 1 | 86 | 85 | 85
F81LHL/T2 | F96T8/HO | Fluorescent, (1) 96", T8 HO lamp, tandem wired to 2-lamp ballast | Electronic | 1 | 86 | 80 | 80
F81SE | F96T12 | Fluorescent, (1) 96", STD lamp | Mag-ES | 1 | 75 | 91 | 91
F81SHE | F96T12/HO | Fluorescent, (1) 96", STD HO lamp | Mag-ES | 1 | 110 | 132 | 132
F81SHL/T2 | F96T12/HO | Fluorescent, (1) 96", STD HO lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 110 | 98 | 98
F81SHS | F96T12/HO | Fluorescent, (1) 96", STD HO lamp | Mag-STD | 1 | 110 | 145 | 145
F81SL | F96T12 | Fluorescent, (1) 96", STD lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 75 | 70 | 70
F81SL/T2 | F96T12 | Fluorescent, (1) 96", STD lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 75 | 67 | 67
F81SS | F96T12 | Fluorescent, (1) 96", STD lamp | Mag-STD | 1 | 75 | 100 | 100
F81SVS | F96T12/VHO | Fluorescent, (1) 96", STD VHO lamp | Mag-STD | 1 | 215 | 230 | 230
F82EE | F96T12/ES | Fluorescent, (2) 96", ES lamp | Mag-ES | 2 | 60 | 123 | 123
F82EHE | F96T12/HO/ES | Fluorescent, (2) 96", ES HO lamp | Mag-ES | 2 | 95 | 207 | 207
F82EHL | F96T12/HO/ES | Fluorescent, (2) 96", ES HO lamp | Electronic | 2 | 95 | 170 | 170
F82EHS | F96T12/HO/ES | Fluorescent, (2) 96", ES HO lamp | Mag-STD | 2 | 95 | 227 | 227
F82EL | F96T12/ES | Fluorescent, (2) 96", ES lamp | Electronic | 2 | 60 | 110 | 110
F82ES | F96T12/ES | Fluorescent, (2) 96", ES lamp | Mag-STD | 2 | 60 | 138 | 138
F82EVS | F96T12/VHO/ES | Fluorescent, (2) 96", ES VHO lamp | Mag-STD | 2 | 185 | 390 | 390
F82ILL | F96T8 | Fluorescent, (2) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 2 | 59 | 109 | 109
F82ILL-R | F96T8 | Fluorescent, (2) 96", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 2 | 59 | 98 | 98
F82LHL | F96T8/HO | Fluorescent, (2) 96", T8 HO lamp | Electronic | 2 | 86 | 160 | 160
F82SE | F96T12 | Fluorescent, (2) 96", STD lamp | Mag-ES | 2 | 75 | 158 | 158
F82SHE | F96T12/HO | Fluorescent, (2) 96", STD HO lamp | Mag-ES | 2 | 110 | 237 | 237
F82SHL | F96T12/HO | Fluorescent, (2) 96", STD HO lamp | Electronic | 2 | 110 | 195 | 195
F82SHS | F96T12/HO | Fluorescent, (2) 96", STD HO lamp | Mag-STD | 2 | 110 | 257 | 257
F82SL | F96T12 | Fluorescent, (2) 96", STD lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 2 | 75 | 134 | 134
F82SS | F96T12 | Fluorescent, (2) 96", STD lamp | Mag-STD | 2 | 75 | 173 | 173
F82SVS | F96T12/VHO | Fluorescent, (2) 96", STD VHO lamp | Mag-STD | 2 | 215 | 450 | 450
F83EE | F96T12/ES | Fluorescent, (3) 96", ES lamp | Mag-ES | 3 | 60 | 210 | 210
F83EHE | F96T12/HO/ES | Fluorescent, (3) 96", ES HO lamp, (1) 2-lamp ES Ballast, (1) 1-lamp STD Ballast | Mag-ES/STD | 3 | 95 | 319 | 319
F83EHS | F96T12/HO/ES | Fluorescent, (3) 96", ES HO lamp | Mag-STD | 3 | 95 | 352 | 352
F83EL | F96T12/ES | Fluorescent, (3) 96", ES lamp | Electronic | 3 | 60 | 179 | 179
F83ES | F96T12/ES | Fluorescent, (3) 96", ES lamp | Mag-STD | 3 | 60 | 221 | 221
F83EVS | F96T12/VHO/ES | Fluorescent, (3) 96", ES VHO lamp | Mag-STD | 3 | 185 | 590 | 590
F83ILL | F96T8 | Fluorescent, (3) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 3 | 59 | 167 | 167
F83SHS | F96T12/HO | Fluorescent, (3) 96", STD HO lamp | Mag-STD | 3 | 110 | 392 | 392
F83SS | F96T12 | Fluorescent, (3) 96", STD lamp | Mag-STD | 3 | 75 | 273 | 273
F83SVS | F96T12/VHO | Fluorescent, (3) 96", STD VHO lamp | Mag-STD | 3 | 215 | 680 | 680
F84EE | F96T12/ES | Fluorescent, (4) 96", ES lamp | Mag-ES | 4 | 60 | 246 | 246
F84EHE | F96T12/HO/ES | Fluorescent, (4) 96", ES HO lamp | Mag-ES | 4 | 95 | 414 | 414
F84EHL | F96T12/HO/ES | Fluorescent, (4) 96", ES HO lamp | Electronic | 4 | 95 | 340 | 340
F84EHS | F96T12/HO/ES | Fluorescent, (4) 96", ES HO lamp | Mag-STD | 4 | 95 | 454 | 454
F84EL | F96T12/ES | Fluorescent, (4) 96", ES lamp | Electronic | 4 | 60 | 220 | 220
F84ES | F96T12/ES | Fluorescent, (4) 96", ES lamp | Mag-STD | 4 | 60 | 276 | 276
F84EVS | F96T12/VHO/ES | Fluorescent, (4) 96", ES VHO lamp | Mag-STD | 4 | 185 | 780 | 780
F84ILL | F96T8 | Fluorescent, (4) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 4 | 59 | 219 | 219
F84LHL | F96T8/HO | Fluorescent, (4) 96", T8 HO lamp | Electronic | 4 | 86 | 320 | 320
F84SE | F96T12 | Fluorescent, (4) 96", STD lamp | Mag-ES | 4 | 75 | 316 | 316
F84SHE | F96T12/HO | Fluorescent, (4) 96", STD HO lamp | Mag-ES | 4 | 110 | 474 | 474
F84SHL | F96T12/HO | Fluorescent, (4) 96", STD HO lamp | Electronic | 4 | 110 | 390 | 390
F84SHS | F96T12/HO | Fluorescent, (4) 96", STD HO lamp | Mag-STD | 4 | 110 | 514 | 514
F84SL | F96T12 | Fluorescent, (4) 96", STD lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 4 | 75 | 268 | 268
F84SS | F96T12 | Fluorescent, (4) 96", STD lamp | Mag-STD | 4 | 75 | 346 | 346
F84SVS | F96T12/VHO | Fluorescent, (4) 96", STD VHO lamp | Mag-STD | 4 | 215 | 900 | 900
F86EHS | F96T12/HO/ES | Fluorescent, (6) 96", ES HO lamp | Mag-STD | 6 | 95 | 721 | 721
F86ILL | F96T8 | Fluorescent, (6) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 6 | 59 | 328 | 328
F86EE | F96T12/ES | Fluorescent, (6) 96", ES lamp | Mag-ES | 6 | 60 | 369 | 369
F86EL | F96T12/ES | Fluorescent, (6) 96", ES lamp | Electronic | 6 | 60 | 330 | 330
Circline Fluorescent Fixtures
FC12/1 | FC12T9 | Fluorescent, (1) 12" circular lamp, RS ballast | Mag-STD | 1 | 32 | 31 | 31
FC12/2 | FC12T9 | Fluorescent, (2) 12" circular lamp, RS ballast | Mag-STD | 2 | 32 | 62 | 62
FC16/1 | FC16T9 | Fluorescent, (1) 16" circular lamp | Mag-STD | 1 | 40 | 35 | 35
FC20 | FC6T9 | Fluorescent, Circlite, (1) 20W lamp, Preheat ballast | Mag-STD | 1 | 20 | 20 | 20
FC22/1 | FC8T9 | Fluorescent, Circlite, (1) 22W lamp, preheat ballast | Mag-STD | 1 | 22 | 20 | 20
FC22/32/1 | FC22/32T9 | Fluorescent, Circlite, (1) 22W/32W lamp, preheat ballast | Mag-STD | 1 | 22/32 | 58 | 58
FC32/1 | FC12T9 | Fluorescent, Circline, (1) 32W lamp, preheat ballast | Mag-STD | 1 | 32 | 40 | 40
FC32/40/1 | FC32/40T9 | Fluorescent, Circlite, (1) 32W/40W lamp, preheat ballast | Mag-STD | 1 | 32/40 | 80 | 80
FC40/1 | FC16T9 | Fluorescent, Circline, (1) 32W lamp, preheat ballast | Mag-STD | 1 | 32 | 42 | 42
FC44/1 | FC44T9 | Fluorescent, Circlite, (1) 44W lamp, preheat ballast | Mag-STD | 1 | 44 | 46 | 46
FC6/1 | FC6T9 | Fluorescent, (1) 6" circular lamp, RS ballast | Mag-STD | 1 | 20 | 25 | 25
FC8/1 | FC8T9 | Fluorescent, (1) 8" circular lamp, RS ballast | Mag-STD | 1 | 22 | 26 | 26
FC8/2 | FC8T9 | Fluorescent, (2) 8" circular lamp, RS ballast | Mag-STD | 2 | 22 | 52 | 52
U-Tube Fluorescent Fixtures
FU1EE | FU40T12/ES | Fluorescent, (1) U-Tube, ES lamp | Mag-ES | 1 | 34 | 43 | 43
FU1ILL | FU31T8/6 | Fluorescent, (1) U-Tube, T-8 lamp, Instant Start ballast | Electronic | 1 | 32 | 31 | 31
FU1LL | FU31T8/6 | Fluorescent, (1) U-Tube, T-8 lamp | Electronic | 1 | 32 | 32 | 32
FU1LL-R | FU31T8/6 | Fluorescent, (1) U-Tube, T-8 lamp, RLO (BF<0.85) | Electronic | 1 | 31 | 27 | 27
FU2SS | FU40T12 | Fluorescent, (2) U-Tube, STD lamp | Mag-STD | 2 | 40 | 96 | 96
FU2SE | FU40T12 | Fluorescent, (2) U-Tube, STD lamp | Mag-ES | 2 | 40 | 85 | 85
FU2EE | FU40T12/ES | Fluorescent, (2) U-Tube, ES lamp | Mag-ES | 2 | 34 | 72 | 72
FU2ES | FU40T12/ES | Fluorescent, (2) U-Tube, ES lamp | Mag-STD | 2 | 34 | 82 | 82
FU2ILL | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, Instant Start Ballast | Electronic | 2 | 32 | 59 | 59
FU2ILL/T4 | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, Instant Start Ballast, tandem wired | Electronic | 2 | 32 | 56 | 56
FU2ILL/T4-R | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, Instant Start Ballast, RLO, tandem wired | Electronic | 2 | 32 | 51 | 51
FU2ILL-H | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, Instant Start HLO Ballast | Electronic | 2 | 32 | 65 | 65
FU2ILL-R | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, Instant Start RLO Ballast | Electronic | 2 | 32 | 52 | 52
FU2LL | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp | Electronic | 2 | 32 | 60 | 60
FU2LL/T2 | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, Tandem 4 lamp ballast | Electronic | 2 | 32 | 59 | 59
FU2LL-R | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, RLO (BF<0.85) | Electronic | 2 | 31 | 54 | 54
FU3EE | FU40T12/ES | Fluorescent, (3) U-Tube, ES lamp | Mag-ES | 3 | 35 | 115 | 115
FU3ILL | FU31T8/6 | Fluorescent, (3) U-Tube, T-8 lamp, Instant Start Ballast | Electronic | 3 | 32 | 89 | 89
FU3ILL-R | FU31T8/6 | Fluorescent, (3) U-Tube, T-8 lamp, Instant Start RLO Ballast | Electronic | 3 | 32 | 78 | 78
Standard Incandescent Fixtures
I100/1 | I100 | Incandescent, (1) 100W lamp |  | 1 | 100 | 100 | 100
I100/2 | I100 | Incandescent, (2) 100W lamp |  | 2 | 100 | 200 | 200
I100/3 | I100 | Incandescent, (3) 100W lamp |  | 3 | 100 | 300 | 300
I100/4 | I100 | Incandescent, (4) 100W lamp |  | 4 | 100 | 400 | 400
I100/5 | I100 | Incandescent, (5) 100W lamp |  | 5 | 100 | 500 | 500
I1000/1 | I1000 | Incandescent, (1) 1000W lamp |  | 1 | 1000 | 1000 | 1000
I100E/1 | I100/ES | Incandescent, (1) 100W ES lamp |  | 1 | 90 | 90 | 90
I100EL/1 | I100/ES/LL | Incandescent, (1) 100W ES/LL lamp |  | 1 | 90 | 90 | 90
I120/1 | I120 | Incandescent, (1) 120W lamp |  | 1 | 120 | 120 | 120
I120/2 | I120 | Incandescent, (2) 120W lamp |  | 2 | 120 | 240 | 240
I125/1 | I125 | Incandescent, (1) 125W lamp |  | 1 | 125 | 125 | 125
I135/1 | I135 | Incandescent, (1) 135W lamp |  | 1 | 135 | 135 | 135
I135/2 | I135 | Incandescent, (2) 135W lamp |  | 2 | 135 | 270 | 270
I15/1 | I15 | Incandescent, (1) 15W lamp |  | 1 | 15 | 15 | 15
I15/2 | I15 | Incandescent, (2) 15W lamp |  | 2 | 15 | 30 | 30
I150/1 | I150 | Incandescent, (1) 150W lamp |  | 1 | 150 | 150 | 150
I150/2 | I150 | Incandescent, (2) 150W lamp |  | 2 | 150 | 300 | 300
I1500/1 | I1500 | Incandescent, (1) 1500W lamp |  | 1 | 1500 | 1500 | 1500
I150E/1 | I150/ES | Incandescent, (1) 150W ES lamp |  | 1 | 135 | 135 | 135
I150EL/1 | I150/ES/LL | Incandescent, (1) 150W ES/LL lamp |  | 1 | 135 | 135 | 135
I170/1 | I170 | Incandescent, (1) 170W lamp |  | 1 | 170 | 170 | 170
I20/1 | I20 | Incandescent, (1) 20W lamp |  | 1 | 20 | 20 | 20
I20/2 | I20 | Incandescent, (2) 20W lamp |  | 2 | 20 | 40 | 40
I200/1 | I200 | Incandescent, (1) 200W lamp |  | 1 | 200 | 200 | 200
I200/2 | I200 | Incandescent, (2) 200W lamp |  | 2 | 200 | 400 | 400
I2000/1 | I2000 | Incandescent, (1) 2000W lamp |  | 1 | 2000 | 2000 | 2000
I200L/1 | I200/LL | Incandescent, (1) 200W LL lamp |  | 1 | 200 | 200 | 200
I25/1 | I25 | Incandescent, (1) 25W lamp |  | 1 | 25 | 25 | 25
I25/2 | I25 | Incandescent, (2) 25W lamp |  | 2 | 25 | 50 | 50
I25/4 | I25 | Incandescent, (4) 25W lamp |  | 4 | 25 | 100 | 100
I250/1 | I250 | Incandescent, (1) 250W lamp |  | 1 | 250 | 250 | 250
I300/1 | I300 | Incandescent, (1) 300W lamp |  | 1 | 300 | 300 | 300
I34/1 | I34 | Incandescent, (1) 34W lamp |  | 1 | 34 | 34 | 34
I34/2 | I34 | Incandescent, (2) 34W lamp |  | 2 | 34 | 68 | 68
I36/1 | I36 | Incandescent, (1) 36W lamp |  | 1 | 36 | 36 | 36
I40/1 | I40 | Incandescent, (1) 40W lamp |  | 1 | 40 | 40 | 40
I40/2 | I40 | Incandescent, (2) 40W lamp |  | 2 | 40 | 80 | 80
I400/1 | I400 | Incandescent, (1) 400W lamp |  | 1 | 400 | 400 | 400
I40E/1 | I40/ES | Incandescent, (1) 40W ES lamp |  | 1 | 34 | 34 | 34
I40EL/1 | I40/ES/LL | Incandescent, (1) 40W ES/LL lamp |  | 1 | 34 | 34 | 34
I42/1 | I42 | Incandescent, (1) 42W lamp |  | 1 | 42 | 42 | 42
I448/1 | I448 | Incandescent, (1) 448W lamp |  | 1 | 448 | 448 | 448
I45/1 | I45 | Incandescent, (1) 45W lamp |  | 1 | 45 | 45 | 45
I50/1 | I50 | Incandescent, (1) 50W lamp |  | 1 | 50 | 50 | 50
I50/2 | I50 | Incandescent, (2) 50W lamp |  | 2 | 50 | 100 | 100
I500/1 | I500 | Incandescent, (1) 500W lamp |  | 1 | 500 | 500 | 500
I52/1 | I52 | Incandescent, (1) 52W lamp |  | 1 | 52 | 52 | 52
I52/2 | I52 | Incandescent, (2) 52W lamp |  | 2 | 52 | 104 | 104
I54/1 | I54 | Incandescent, (1) 54W lamp |  | 1 | 54 | 54 | 54
I54/2 | I54 | Incandescent, (2) 54W lamp |  | 2 | 54 | 108 | 108
I55/1 | I55 | Incandescent, (1) 55W lamp |  | 1 | 55 | 55 | 55
I55/2 | I55 | Incandescent, (2) 55W lamp |  | 2 | 55 | 110 | 110
I60/1 | I60 | Incandescent, (1) 60W lamp |  | 1 | 60 | 60 | 60
I60/2 | I60 | Incandescent, (2) 60W lamp |  | 2 | 60 | 120 | 120
I60/3 | I60 | Incandescent, (3) 60W lamp |  | 3 | 60 | 180 | 180
I60/4 | I60 | Incandescent, (4) 60W lamp |  | 4 | 60 | 240 | 240
I60/5 | I60 | Incandescent, (5) 60W lamp |  | 5 | 60 | 300 | 300
I60E/1 | I60/ES | Incandescent, (1) 60W ES lamp |  | 1 | 52 | 52 | 52
I60EL/1 | I60/ES/LL | Incandescent, (1) 60W ES/LL lamp |  | 1 | 52 | 52 | 52
I65/1 | I65 | Incandescent, (1) 65W lamp |  | 1 | 65 | 65 | 65
I65/2 | I65 | Incandescent, (2) 65W lamp |  | 2 | 65 | 130 | 130
I67/1 | I67 | Incandescent, (1) 67W lamp |  | 1 | 67 | 67 | 67
I67/2 | I67 | Incandescent, (2) 67W lamp |  | 2 | 67 | 134 | 134
I67/3 | I67 | Incandescent, (3) 67W lamp |  | 3 | 67 | 201 | 201
I69/1 | I69 | Incandescent, (1) 69W lamp |  | 1 | 69 | 69 | 69
I7.5/1 | I7.5 | Tungsten exit light, (1) 7.5 W lamp, used in night light application |  | 1 | 7.5 | 8 | 8
I7.5/2 | I7.5 | Tungsten exit light, (2) 7.5 W lamp, used in night light application |  | 2 | 7.5 | 15 | 15
I72/1 | I72 | Incandescent, (1) 72W lamp |  | 1 | 72 | 72 | 72
I75/1 | I75 | Incandescent, (1) 75W lamp |  | 1 | 75 | 75 | 75
I75/2 | I75 | Incandescent, (2) 75W lamp |  | 2 | 75 | 150 | 150
I75/3 | I75 | Incandescent, (3) 75W lamp |  | 3 | 75 | 225 | 225
I75/4 | I75 | Incandescent, (4) 75W lamp |  | 4 | 75 | 300 | 300
I750/1 | I750 | Incandescent, (1) 750W lamp |  | 1 | 750 | 750 | 750
I75E/1 | I75/ES | Incandescent, (1) 75W ES lamp |  | 1 | 67 | 67 | 67
I75EL/1 | I75/ES/LL | Incandescent, (1) 75W ES/LL lamp |  | 1 | 67 | 67 | 67
I80/1 | I80 | Incandescent, (1) 80W lamp |  | 1 | 80 | 80 | 80
I85/1 | I85 | Incandescent, (1) 85W lamp |  | 1 | 85 | 85 | 85
I90/1 | I90 | Incandescent, (1) 90W lamp |  | 1 | 90 | 90 | 90
I90/2 | I90 | Incandescent, (2) 90W lamp |  | 2 | 90 | 180 | 180
I90/3 | I90 | Incandescent, (3) 90W lamp |  | 3 | 90 | 270 | 270
I93/1 | I93 | Incandescent, (1) 93W lamp |  | 1 | 93 | 93 | 93
I95/1 | I95 | Incandescent, (1) 95W lamp |  | 1 | 95 | 95 | 95
I95/2 | I95 | Incandescent, (2) 95W lamp |  | 2 | 95 | 190 | 190
Halogen Incandescent Fixtures
H100/1 | H100 | Halogen Incandescent, (1) 100W lamp |  | 1 | 100 | 100 | 100
H1000/1 | H1000 | Halogen Incandescent, (1) 1000W lamp |  | 1 | 1000 | 1000 | 1000
H1200/1 | H1200 | Halogen Incandescent, (1) 1200W lamp |  | 1 | 1200 | 1200 | 1200
H150/1 | H150 | Halogen Incandescent, (1) 150W lamp |  | 1 | 150 | 150 | 150
H150/2 | H150 | Halogen Incandescent, (2) 150W lamp |  | 2 | 150 | 300 | 300
H1500/1 | H1500 | Halogen Incandescent, (1) 1500W lamp |  | 1 | 1500 | 1500 | 1500
H200/1 | H200 | Halogen Incandescent, (1) 200W lamp |  | 1 | 200 | 200 | 200
H250/1 | H250 | Halogen Incandescent, (1) 250W lamp |  | 1 | 250 | 250 | 250
H300/1 | H300 | Halogen Incandescent, (1) 300W lamp |  | 1 | 300 | 300 | 300
H35/1 | H35 | Halogen Incandescent, (1) 35W lamp |  | 1 | 35 | 35 | 35
H350/1 | H350 | Halogen Incandescent, (1) 350W lamp |  | 1 | 350 | 350 | 350
H40/1 | H40 | Halogen Incandescent, (1) 40W lamp |  | 1 | 40 | 40 | 40
H400/1 | H400 | Halogen Incandescent, (1) 400W lamp |  | 1 | 400 | 400 | 400
H42/1 | H42 | Halogen Incandescent, (1) 42W lamp |  | 1 | 42 | 42 | 42
H425/1 | H425 | Halogen Incandescent, (1) 425W lamp |  | 1 | 425 | 425 | 425
H45/1 | H45 | Halogen Incandescent, (1) 45W lamp |  | 1 | 45 | 45 | 45
H45/2 | H45 | Halogen Incandescent, (2) 45W lamp |  | 2 | 45 | 90 | 90
H50/1 | H50 | Halogen Incandescent, (1) 50W lamp |  | 1 | 50 | 50 | 50
H50/2 | H50 | Halogen Incandescent, (2) 50W lamp |  | 2 | 50 | 100 | 100
H500/1 | H500 | Halogen Incandescent, (1) 500W lamp |  | 1 | 500 | 500 | 500
H52/1 | H52 | Halogen Incandescent, (1) 52W lamp |  | 1 | 52 | 52 | 52
H55/1 | H55 | Halogen Incandescent, (1) 55W lamp |  | 1 | 55 | 55 | 55
H55/2 | H55 | Halogen Incandescent, (2) 55W lamp |  | 2 | 55 | 110 | 110
H60/1 | H60 | Halogen Incandescent, (1) 60W lamp |  | 1 | 60 | 60 | 60
H72/1 | H72 | Halogen Incandescent, (1) 72W lamp |  | 1 | 72 | 72 | 72
H75/1 | H75 | Halogen Incandescent, (1) 75W lamp |  | 1 | 75 | 75 | 75
H75/2 | H75 | Halogen Incandescent, (2) 75W lamp |  | 2 | 75 | 150 | 150
H750/1 | H750 | Halogen Incandescent, (1) 750W lamp |  | 1 | 750 | 750 | 750
H90/1 | H90 | Halogen Incandescent, (1) 90W lamp |  | 1 | 90 | 90 | 90
H90/2 | H90 | Halogen Incandescent, (2) 90W lamp |  | 2 | 90 | 180 | 180
H900/1 | H900 | Halogen Incandescent, (1) 900W lamp |  | 1 | 900 | 900 | 900
HLV20/1 | H20/LV | Halogen Low Voltage Incandescent, (1) 20W lamp |  | 1 | 20 | 30 | 30
HLV25/1 | H25/LV | Halogen Low Voltage Incandescent, (1) 25W lamp |  | 1 | 25 | 35 | 35
HLV35/1 | H35/LV | Halogen Low Voltage Incandescent, (1) 35W lamp |  | 1 | 35 | 45 | 45
HLV42/1 | H42/LV | Halogen Low Voltage Incandescent, (1) 42W lamp |  | 1 | 42 | 52 | 52
HLV50/1 | H50/LV | Halogen Low Voltage Incandescent, (1) 50W lamp |  | 1 | 50 | 60 | 60
HLV65/1 | H65/LV | Halogen Low Voltage Incandescent, (1) 65W lamp |  | 1 | 65 | 75 | 75
HLV75/1 | H75/LV | Halogen Low Voltage Incandescent, (1) 75W lamp |  | 1 | 75 | 85 | 85
QL Induction Fixtures
QL55/1 | QL55 | QL Induction, (1) 55W lamp | Generator | 1 | 55 | 55 | 55
QL85/1 | QL85 | QL Induction, (1) 85W lamp | Generator | 1 | 85 | 85 | 85
QL165/1 | QL165 | QL Induction, (1) 165W lamp | Generator | 1 | 165 | 165 | 165
High Pressure Sodium Fixtures
HPS100/1 | HPS100 | High Pressure Sodium, (1) 100W lamp | CWA | 1 | 100 | 138 | 138
HPS1000/1 | HPS1000 | High Pressure Sodium, (1) 1000W lamp | CWA | 1 | 1000 | 1100 | 1100
HPS150/1 | HPS150 | High Pressure Sodium, (1) 150W lamp | CWA | 1 | 150 | 188 | 188
HPS200/1 | HPS200 | High Pressure Sodium, (1) 200W lamp | CWA | 1 | 200 | 250 | 250
HPS225/1 | HPS225 | High Pressure Sodium, (1) 225W lamp | CWA | 1 | 225 | 275 | 275
HPS250/1 | HPS250 | High Pressure Sodium, (1) 250W lamp | CWA | 1 | 250 | 295 | 295
HPS310/1 | HPS310 | High Pressure Sodium, (1) 310W lamp | CWA | 1 | 310 | 365 | 365
HPS35/1 | HPS35 | High Pressure Sodium, (1) 35W lamp | CWA | 1 | 35 | 46 | 46
HPS360/1 | HPS360 | High Pressure Sodium, (1) 360W lamp | CWA | 1 | 360 | 414 | 414
HPS400/1 | HPS400 | High Pressure Sodium, (1) 400W lamp | CWA | 1 | 400 | 465 | 465
HPS50/1 | HPS50 | High Pressure Sodium, (1) 50W lamp | CWA | 1 | 50 | 66 | 66
HPS600/1 | HPS600 | High Pressure Sodium, (1) 600W lamp | CWA | 1 | 600 | 675 | 675
HPS70/1 | HPS70 | High Pressure Sodium, (1) 70W lamp | CWA | 1 | 70 | 95 | 95
HPS750/1 | HPS750 | High Pressure Sodium, (1) 750W lamp | CWA | 1 | 750 | 835 | 835
Metal Halide Fixtures
MH100/1 | MH100 | Metal Halide, (1) 100W lamp | CWA | 1 | 100 | 128 | 128
MH1000/1 | MH1000 | Metal Halide, (1) 1000W lamp | CWA | 1 | 1000 | 1080 | 1080
MH150/1 | MH150 | Metal Halide, (1) 150W lamp | CWA | 1 | 150 | 190 | 190
MH1500/1 | MH1500 | Metal Halide, (1) 1500W lamp | CWA | 1 | 1500 | 1610 | 1610
MH175/1 | MH175 | Metal Halide, (1) 175W lamp | CWA | 1 | 175 | 215 | 215
MH1800/1 | MH1800 | Metal Halide, (1) 1800W lamp | CWA | 1 | 1800 | 1875 | 1875
MH200/1 | MH200 | Metal Halide, (1) 200W lamp | CWA | 1 | 200 | 232 | 232
MH250/1 | MH250 | Metal Halide, (1) 250W lamp | CWA | 1 | 250 | 295 | 295
MH32/1 | MH32 | Metal Halide, (1) 32W lamp | CWA | 1 | 32 | 43 | 43
MH300/1 | MH300 | Metal Halide, (1) 300W lamp | CWA | 1 | 300 | 342 | 342
MH320/1 | MH320 | Metal Halide, (1) 320W lamp | CWA | 1 | 320 | 365 | 365
MH350/1 | MH350 | Metal Halide, (1) 350W lamp | CWA | 1 | 350 | 400 | 400
MH360/1 | MH360 | Metal Halide, (1) 360W lamp | CWA | 1 | 360 | 430 | 430
MH400/1 | MH400 | Metal Halide, (1) 400W lamp | CWA | 1 | 400 | 458 | 458
MH400/2 | MH400 | Metal Halide, (2) 400W lamp | CWA | 2 | 400 | 916 | 916
MH450/1 | MH450 | Metal Halide, (1) 450W lamp | CWA | 1 | 450 | 508 | 508
MH35/1 | MH35 | Metal Halide, (1) 35W lamp | CWA | 1 | 35 | 44 | 44
MH50/1 | MH50 | Metal Halide, (1) 50W lamp | CWA | 1 | 50 | 72 | 72
MH70/1 | MH70 | Metal Halide, (1) 70W lamp | CWA | 1 | 70 | 95 | 95
MH750/1 | MH750 | Metal Halide, (1) 750W lamp | CWA | 1 | 750 | 850 | 850
MHPS/LR/100/1 | MHPS100 | Metal Halide Pulse Start, (1) 100W lamp w/ Linear Reactor Ballast | LR | 1 | 100 | 118 | 118
MHPS/LR/150/1 | MHPS150 | Metal Halide Pulse Start, (1) 150W lamp w/ Linear Reactor Ballast | LR | 1 | 150 | 170 | 170
MHPS/LR/175/1 | MHPS175 | Metal Halide Pulse Start, (1) 175W lamp w/ Linear Reactor Ballast | LR | 1 | 175 | 194 | 194
MHPS/LR/200/1 | MHPS200 | Metal Halide Pulse Start, (1) 200W lamp w/ Linear Reactor Ballast | LR | 1 | 200 | 219 | 219
MHPS/LR/250/1 | MHPS250 | Metal Halide Pulse Start, (1) 250W lamp w/ Linear Reactor Ballast | LR | 1 | 250 | 275 | 275
MHPS/LR/300/1 | MHPS300 | Metal Halide Pulse Start, (1) 300W lamp w/ Linear Reactor Ballast | LR | 1 | 300 | 324 | 324
MHPS/LR/320/1 | MHPS320 | Metal Halide Pulse Start, (1) 320W lamp w/ Linear Reactor Ballast | LR | 1 | 320 | 349 | 349
MHPS/LR/350/1 | MHPS350 | Metal Halide Pulse Start, (1) 350W lamp w/ Linear Reactor Ballast | LR | 1 | 350 | 380 | 380
MHPS/LR/400/1 | MHPS400 | Metal Halide Pulse Start, (1) 400W lamp w/ Linear Reactor Ballast | LR | 1 | 400 | 435 | 435
MHPS/LR/450/1 | MHPS450 | Metal Halide Pulse Start, (1) 450W lamp w/ Linear Reactor Ballast | LR | 1 | 450 | 485 | 485
MHPS/LR/750/1 | MHPS750 | Metal Halide Pulse Start, (1) 750W lamp w/ Linear Reactor Ballast | LR | 1 | 750 | 805 | 805
MHPS/SCWA/100/1 | MHPS100 | Metal Halide Pulse Start, (1) 100W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 | 100 | 128 | 128
MHPS/SCWA/1000/1 | MHPS1000 | Metal Halide Pulse Start, (1) 1000W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 | 1000 | 1080 | 1080
MHPS/SCWA/150/1 | MHPS150 | Metal Halide Pulse Start, (1) 150W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 | 150 | 190 | 190
MHPS/SCWA/175/1 | MHPS175 | Metal Halide Pulse Start, (1) 175W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 | 175 | 208 | 208
MHPS/SCWA/200/1 | MHPS200 | Metal Halide Pulse Start, (1) 200W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 | 200 | 232 | 232
MHPS/SCWA/250/1 | MHPS250 | Metal Halide Pulse Start, (1) 250W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 | 250 | 288 | 288
MHPS/SCWA/300/1 | MHPS300 | Metal Halide Pulse Start, (1) 300W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 | 300 | 342 | 342
MHPS/SCWA/320/1 | MHPS320 | Metal Halide Pulse Start, (1) 320W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 | 320 | 368 | 368
MHPS/SCWA/350/1 | MHPS350 | Metal Halide Pulse Start, (1) 350W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 | 350 | 400 | 400
MHPS/SCWA/400/1 | MHPS400 | Metal Halide Pulse Start, (1) 400W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 | 400 | 450 | 450
MHPS/SCWA/450/1 | MHPS450 | Metal Halide Pulse Start, (1) 450W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 | 450 | 506 | 506
MHPS/SCWA/750/1 | MHPS750 | Metal Halide Pulse Start, (1) 750W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 | 750 | 815 | 815
Mercury Vapor Fixtures
MV100/1 | MV100 | Mercury Vapor, (1) 100W lamp | CWA | 1 | 100 | 125 | 125
MV1000/1 | MV1000 | Mercury Vapor, (1) 1000W lamp | CWA | 1 | 1000 | 1075 | 1075
MV175/1 | MV175 | Mercury Vapor, (1) 175W lamp | CWA | 1 | 175 | 205 | 205
MV250/1 | MV250 | Mercury Vapor, (1) 250W lamp | CWA | 1 | 250 | 290 | 290
MV40/1 | MV40 | Mercury Vapor, (1) 40W lamp | CWA | 1 | 40 | 50 | 50
MV400/1 | MV400 | Mercury Vapor, (1) 400W lamp | CWA | 1 | 400 | 455 | 455
MV400/2 | MV400 | Mercury Vapor, (2) 400W lamp | CWA | 2 | 400 | 910 | 910
MV50/1 | MV50 | Mercury Vapor, (1) 50W lamp | CWA | 1 | 50 | 74 | 74
MV700/1 | MV700 | Mercury Vapor, (1) 700W lamp | CWA | 1 | 700 | 780 | 780
MV75/1 | MV75 | Mercury Vapor, (1) 75W lamp | CWA | 1 | 75 | 93 | 93
Miscellaneous
N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Add | None | This pre-fixture code should be used as a placeholder when adding new additional fixtures. |  | 0 | 0 | 0 | 0
Removed | None | This post-fixture code should be used when the fixture(s) is(are) completely removed from service. |  | 0 | 0 | 0 | 0
Cut Sheet Fixtures
Cut Sheet 1 | [5 empty] | Edit | Edit
Cut Sheet 2 | [5 empty] | Edit | Edit
Cut Sheet 3 | [5 empty] | Edit | Edit
Cut Sheet 4 | [5 empty] | Edit | Edit
Cut Sheet 5 | [5 empty] | Edit | Edit
Cut Sheet 6 | [5 empty] | Edit | Edit
Cut Sheet 7 | [5 empty] | Edit | Edit
Cut Sheet 8 | [5 empty] | Edit | Edit
Cut Sheet 9 | [5 empty] | Edit | Edit
Cut Sheet 10 | [5 empty] | Edit | Edit
Cut Sheet 11 | [5 empty] | Edit | Edit
Cut Sheet 12 | [5 empty] | Edit | Edit
Cut Sheet 13 | [5 empty] | Edit | Edit
Cut Sheet 14 | [5 empty] | Edit | Edit
Cut Sheet 15 | [5 empty] | Edit | Edit
Cut Sheet 16 | [5 empty] | Edit | Edit
Cut Sheet 17 | [5 empty] | Edit | Edit
Cut Sheet 18 | [5 empty] | Edit | Edit
Cut Sheet 19 | [5 empty] | Edit | Edit
Cut Sheet 20 | [5 empty] | Edit | Edit

## 07 Fixture Code Legend
Fixture Code Legend and Notes
Sample Linear Fluorescent Fixture Code |  |  |  | Sample of Other Fixture Code:
|  | CONFIGURATION (letter) |  | FIXTURE TYPE |  |  | NUMBER OF LAMPS
NUMBER OF LAMPS |  | Tandem Wired |  | Compact Fluorescent, |  |  | 1 Lamp Fixture
|  |  | CONFIGURATION (number) | Quad Tube
FIXTURE TYPE |  |  | 4 Lamps on this Ballast
Fluorescent | [5 empty] | CFQ18/1-L
F41ILL/T4-R
BALLAST LIGHT OUTPUT
LAMP LENGTH |  |  | Reduced Light Output | NATIONAL LAMP WATTAGE |  |  | BALLAST TYPE
4 Feet |  |  |  |  | 18W |  | Electronic Ballast
| LAMP TYPE |  | BALLAST TYPE
| Instant start, T8 |  | Electronic Ballast
Code Explanations
Fixture Type |  |  |  | for LED traffic signals
CF | Compact Fluorescent
CFD | Compact Fluorescent, double-D shape |  |  | 12GA | 12" Green Arrow
CFS | Compact Fluorescent, Spiral |  |  | 12GB | 12" Green Ball
CFT | Compact Fluorescent, Twin tube |  |  | 12RA | 12" Red Arrow
| (including "Biaxial" fixtures) |  |  | 12RB | 12" Red Ball
CFQ | Compact Fluorescent, Quad tube |  |  | 8GB | 8" Green Ball
ECF | Exit sign, Compact Fluorescent |  |  | 8RB | 8" Red Ball
EI | Exit sign, Incandescent |  |  | PH | Pedestrian Hand signal
ELED | Exit sign, LED
F | Fluorescent, linear |  |  | Ballast Type
FC | Fluorescent, Circline |  |  | for fluorescent fixtures
FU | Fluorescent, U-tube |  |  | L | Electronic
H | Halogen |  |  | S | Standard magnetic
HLV | Halogen, Low Voltage |  |  | E | Emergy efficient magnetic
HPS | High Pressure Sodium
I | Incandescent |  |  | Configuration (letter)
LED | Light Emitting Diode (LED) traffic signal |  |  | T | Tandem wired fixture
MH | Metal Halide |  |  | D | Delamped fixture, i.e. some lamps
MHPS | Metal Halide, Pulse Start |  |  |  | permanently removed but ballasts
MV | Mercury Vapor |  |  |  | remain
QL | Induction
Configuration (number)
Lamp Type |  |  |  | for delamped fixtures
for fluorescent fixtures |  |  |  | Number signifies the total number of ballasts
A | "F25T12" - 25 watt, 4ft, T12 lamp |  |  | in the fixture: e.g. An "F42EEID2" is an
IL | T8, Instant start |  |  | "F44EE" with two lamps removed so that there
SIL | T8, Instant start, Super 30 watt |  |  | is one extaneous ballast
SSIL | T8, Instant start, Super 28 watt
L | T8, rapid start |  |  | for tandem wired ballasts
G | T5, standard |  |  | Number signifies the total number of lamps
GH | T5, standard, High output lamp |  |  | being run by the ballast: e.g. An "F42LLIT4"
E | T12, Energy efficient |  |  | would indicate that a four-lamp ballast is
EH | T12, Energy efficient, High output lamp |  |  | wired to run two-lamp fixtures.
EI | T12, Energy efficient, Instant start
EV | T12, Energy efficient, Very high output |  |  | with no preceding letter
S | T12, Standard |  |  | Number indicates the number of ballasts in an
SIL | T12, Standard, Instant start |  |  | ambiguous multiple ballast fixture: e.g. An
SH | T12, Standard, High output lamp |  |  | "F43ILU2" indicates a three-lamp fixture with
SV | T12, Standard, Very high output lamp |  |  | two ballasts (as is often the case if there is A/B
T | T10, Standard |  |  | switching).
Ballast Light Output
|  |  |  | R | Reduced light output
|  |  |  | H | High light output
|  |  |  | V | Very high light output
Notes:
1) The column labeled Watts/Fixtures in the data table includes ballast loads.
2) The fixture wattage values represent an average value, rounded to the nearest whole watt.

## 08 Fixture Code Locator
Pennsylvania Act 129 Lighting Audit and Design Tool for New Construction Projects
LIGHTING FIXTURE CODE LOCATOR | [14 empty] | Password: Act129Lighting
*Required | Fill In Tan Fields
**Required for all except U-Tube |  |  | SELECTED | [5 empty] | FIXTURE TYPE |  |  |  | LAMP TYPE |  | CONFIGURATION (NUMBER)
Linear Fluorescent Fixtures Only |  |  | Compact Fluorescent | Standard | Double-D shape | Spiral | Twin tube (including "Biaxial") | Quad tube | Compact Fluorescent | Standard | Compact FluorescentStandard | CF | T5, Standard | G | for delamped fixtures
|  |  | Fluorescent | Circline | U-Tube |  |  |  | Compact Fluorescent | Double-D shape | Compact FluorescentDouble-D shape | CFD | T5, Standard, High output lamp | GH | Number signifies the total number of ballasts
Fixture Type*: | Fluorescent |  | Halogen | Standard | Low Voltage |  |  |  | Compact Fluorescent | Spiral | Compact FluorescentSpiral | CFS | T8, Instant Start | IL | in the fixture: e.g. An "F42EEID2" is an
Fixture Subtype*: | Linear | F | High Pressure Sodium | Standard |  |  |  |  | Compact Fluorescent | Twin tube (including "Biaxial") | Compact FluorescentTwin tube (including "Biaxial") | CFT | T8, Instant Start, Super 30 watt | SIL | "F44EE" with two lamps removed so that there
Lamp Length*: |  |  | Incandescent | Standard |  |  |  |  | Compact Fluorescent | Quad tube | Compact FluorescentQuad tube | CFQ | T8, Instant Start, Super 28 watt | SSIL | is one extaneous ballast
Number of Lamps*: |  |  | Induction | Standard |  |  |  |  | Exit Sign | Compact Fluorescent | Exit SignCompact Fluorescent | ECF | T8, Rapid Start | L
Lamp Type*: |  |  | Metal Halide | Standard | Pulse Start |  |  |  | Exit Sign | Incandescent | Exit SignIncandescent | EI | T10, Standard | T | for tandem wired ballasts
Ballast Type*: |  |  | Mercury Vapor | Standard |  |  |  |  | Exit Sign | LED | Exit SignLED | ELED | T12, Energy Efficient | E | Number signifies the total number of lamps
Configuration (Letter): |  |  | Exit Sign | Compact Fluorescent | Incandescent | LED |  |  | Fluorescent | Linear | FluorescentLinear | F | T12, Energy Efficient, High output lamp | EH | being run by the ballast: e.g. An "F42LLIT4"
Configuration (Number): |  |  | Traffic Signal LED | 12" Green Arrow | 12" Green Ball | 12" Red Arrow | 12" Red Ball | Pedestrian Hand signal | Fluorescent | Circline | FluorescentCircline | FC | T12, Energy Efficient, Instant start | EI | would indicate that a four-lamp ballast is
Ballast Light Output: | [8 empty] | Fluorescent | U-Tube | FluorescentU-Tube | FU | T12, Energy Efficient, Very high output | EV | wired to run two-lamp fixtures.
|  |  | BALLAST TYPE | [5 empty] | Halogen | Standard | HalogenStandard | H | T12, Standard | S
Fixture Code: | Fill In All Applicable Fields | F | Electronic | L |  |  |  |  | Halogen | Low Voltage | HalogenLow Voltage | HLV | T12, Standard, Instant start | SIL | with no preceding letter
|  |  | Standard Magnetic | S |  |  |  |  | High Pressure Sodium | Standard | High Pressure SodiumStandard | HPS | T12, Standard, High output lamp | SH | Number indicates the number of ballasts in an
|  |  | Energy Efficient Magnetic | E |  |  |  |  | Incandescent | Standard | IncandescentStandard | I | T12, Standard, Very high output lamp | SV | ambiguous multiple ballast fixture: e.g. An
All Other Fixtures | [8 empty] | Traffic Signal | LED | Traffic SignalLED | LED |  |  | "F43ILU2" indicates a three-lamp fixture with
|  |  | BALLAST LIGHT OUTPUT | [5 empty] | Metal Halide | Standard | Metal HalideStandard | MH |  |  | two ballasts (as is often the case if there is A/B
Fixture Type*: |  |  | Reduced Light Output | -R |  |  |  |  | Metal Halide | Pulse Start | Metal HalidePulse Start | MHPS |  |  | switching).
Fixture Subtype*: |  |  | High Light Output | -H |  |  |  |  | Mercury Vapor | Standard | Mercury VaporStandard | MV
Nominal Lamp Wattage*: |  |  | Very High Light Output | -V |  |  |  |  | Induction | Standard | InductionStandard | QL |  |  | See "Fixture Code Legend" sheet for additional help.
Number of Lamps**: | [8 empty] | Traffic Signal LED | 12" Green Arrow | Traffic Signal LED12" Green Arrow | 12GA
Ballast Type: |  |  | LAMP LENGTH | [5 empty] | Traffic Signal LED | 12" Green Ball | Traffic Signal LED12" Green Ball | 12GB |  |  | Only fixture codes listed in the Standard Wattage Table will be located.
|  |  | 1.5 Feet (18 Inches) | 1.5 |  |  |  |  | Traffic Signal LED | 12" Red Arrow | Traffic Signal LED12" Red Arrow | 12RA
Fixture Code: | Fill In All Applicable Fields |  | 2' Feet (24 Inches) | 2 |  |  |  |  | Traffic Signal LED | 12" Red Ball | Traffic Signal LED12" Red Ball | 12RB
|  |  | 3' Feet (36 Inches) | 3 |  |  |  |  | Traffic Signal LED | Pedestrian Hand signal | Traffic Signal LEDPedestrian Hand signal | PH
|  |  | 4' Feet (48 Inches) | 4
Disclaimer: This fixture code locator is still in development. In some cases, the locator may note that the fixture cannot be found due to the use of non-standard and diverse notations for fixture codes. A manual search of the wattage table is recommended to double-check results. |  |  | 5' Feet (60 Inches) | 5
|  |  | 6' Feet (72 Inches) | 6
|  |  | 8' Feet (96 Inches) | 8
NUMBER OF LAMPS
|  |  | 1 Lamp | 1
|  |  | 2 Lamps | 2
|  |  | 3 Lamps | 3
|  |  | 4 Lamps | 4
|  |  | 5 Lamps | 5
|  |  | 6 Lamps | 6
|  |  | 7 Lamps | 7
|  |  | 8 Lamps | 8
CONFIGURATION (LETTER)
|  |  | Tandem Wired Fixture | T
|  |  | Delamped Fixture | D
Note on B25: Manually Enter Number (No Drop-Down)