## Manual
2021 TRM Appendix C: Lighting Audit & Design Tool for Commercial and Industrial Projects
MANUAL
TABLE OF CONTENTS
| I. | Purpose
| II. | Organization
| III. | User Guide
| IV. | Notes
| V. | Disclaimer
I. PURPOSE
The purpose of the Lighting Audit & Design Tool is two-fold:
1. To document the pre- and post-installation cases of the lighting retrofit.
2. To facilitate the calculation of energy and demand reductions for large lighting installations.
II. ORGANIZATION
The Lighting Audit & Design Tool is organized into 8 sheets.
(1) Manual
FOR REFERENCE ONLY
The "Manual" sheet contains the instructions for using the Lighting Audit & Design Tool.
(2) Changelog
FOR REFERENCE ONLY
The "Changelog" sheet provides an itemized list of major changes from the previous version of the tool.
(3) Glossary
FOR REFERENCE ONLY
The "Glossary" sheet defines key inputs and outputs by column heading for all tabs accepting user inputs. This sheet should be consulted in the event that the user cannot determine what is being asked or presented in any of the fields requiring input or providing outputs.
(4) General Information
USER INPUT REQUIRED
The "General Information" sheet is where the user identifies facility-specific details of the project that have an effect on the calculation of gross savings. Facility-specific details include such things as contact information, electric utility, building area information, and operating schedule.
(5) Lighting Inventory
USER INPUT REQUIRED
The "Lighting Inventory" sheet is the main worksheet that calculates energy savings and peak demand reduction for the user-specified lighting fixture and controls improvements. This form follows the conventions and equations described in the PA TRM and facilitates the calculation of gross savings for implementation and evaluation purposes. All key variable are entered on this sheet.
(6) Fixture Identities
FOR REFERENCE ONLY / USER INPUT REQUIRED FOR CUSTOM AND LED FIXTURES
The "Fixture Identities" sheet contains the master list of fixtures recognized by the Lighting Audit & Design Tool. Each allowable fixture has a unique fixture code, description, and stipulated wattage value. The sheet has filtering functions enabled so users can search for specific fixture codes by any of the associated parameters. The sheet also has input fields for custom fixture codes and non-integrated ballast LEDs that must be accompanied by cut sheets. Note that inclusion of a fixture in this table does not guarantee compliance with specific program requirements.
(7) Summary
FOR REFERENCE ONLY
The "Summary" sheet contains an overview of the customer information, the quantities of measures installed, and the associated total savings achieved by the project.
(8) Lookups
FOR REFERENCE ONLY
The "Lookups" sheet contains reference tables that are used by the tool to assign associated values to selected parameters within the sheets where user input is required.
III. USER GUIDE
1. This tool is required for projects over 20 kW of connected load savings to facilitate calculation of savings pursuant to the PA TRM. Use of this tool for projects under 20 kW should conform to EDC program rules. Consult the TRM for clarification on rules for calculating savings.
2. Begin at the "Project / Site Information" portion of the "General Information" tab, filling in all orange cells. For more detailed information on any of the requirements of the input cells available in this section, select the heading from the full list below, or use the search function in the "Glossary" tab.
G:D13 |  |  |  | Applicant Name | For cell D13, "Applicant Name", specify the name of the applicant as corroborated by the submitted W9. | Phone | For cell D20, "Phone", designate the phone number where the designated contact can be reached.
G:D14 |  |  |  | Facility Name | For cell D14, "Facility Name", specify a name of the facility in question for reference in the event that the applicant will be submitting applications for multiple facilities within one program year. | Email | For cell D21, "Email", designate the email address where the designated contact can be reached.
G:D16 |  |  |  | Address | For cell D16, "Address", specify the address at which the project takes place. | Facility Type | For cell D23, "ASHRAE Facility Type", select the option from the drop-down menu that best describes the usage of the facility.
G:D17 |  |  |  | City | For cell D17, "City", specify the city in which the facility is located. | Construction Type | For cell D24, "Construction Type", specify whether this project is for a lighting retrofit project or for new construction.
G:H17 |  |  |  | State | For cell H17, "State", specify the state in which the facility is located. | Facility Size | For cell D25, "Facility Size", specify the total square footage of the facility at which the project occurs. This field is optional for retrofit applications.
G:J17 |  |  |  | Zip | For cell J17, "Zip", specify the zip code in which the facility is located. | Installation Date | For cell I25, "Heating Fuel Type", specify whether the facility is serviced by gas or electric heat.
G:D18 |  |  |  | Utility | For cell D18, "Utility", specify the electric distribution company who services the facility. | HOU/CF Source | For cell D26, "Installation Date", specify the completion (or expected completion) date of the project.
G:H18 |  |  |  | Account No. | For cell H18, "Account No.", specify the account number on record with electric distributing company. If this is a pre-application for a new construction project, and service has not yet been connect, input "TBD". | Facility for the Visually Impaired | For cell I26, "HOU/CF Source", specify whether this project will be evaluated using TRM-deemed hours of use and coincidence factors, or if custom operating schedules will be designated.
G:D19 |  |  |  | Contact Name and Title | For cell D19, "Contact Name and Title", designate the person who should be contacted in the event that there are any questions regarding this application. | Exterior Lighting Zone
G:I27 |  |  |  | Small Business Direct Install | For cell I27, indicate whether or not this is a small business direct install project. Selecting "Yes" will disable the T12 baseline adjustment feature.
G:D20 |  |  |  | Phone | For cell D20, "Phone", designate the phone number where the designated contact can be reached.
G:D21 |  |  |  | Email | For cell D21, "Email", designate the email address where the designated contact can be reached.
G:D23 |  |  |  | ASHRAE Facility Type | For cell D23, "ASHRAE Facility Type", select the option from the drop-down menu that best describes the usage of the facility.
G:D24 |  |  |  | Construction Type | For cell D24, "Construction Type", specify whether this project is for a lighting retrofit project or for new construction.
G:D25 |  |  |  | Facility Size | For cell D25, "Facility Size", specify the total square footage of the facility at which the project occurs. This field is optional for retrofit applications.
G:D26 |  |  |  | Installation Date | For cell D26, "Installation Date", specify the completion (or expected completion) date of the project.
G:I26 |  |  |  | HOU/CF Source | For cell I26, "HOU/CF Source", specify whether this project will be evaluated using TRM-specified hours of use and coincidence factors, or if custom operating schedules will be designated.
G:I28 |  |  |  | Facility for the Visually Impaired | For cell I28, "Does this facility service the visually impaired?", specify whether this facility services people with visual impairments. This is needed to determine the appropriate ASHRAE LPD.
G:I29 |  |  |  | Exterior Lighting Zone | For cell I29, "Which exterior lighting zone describes your project?", specify the ASHRAE Exterior Lighting Zone to which this building belongs. This is needed to determine the appropriate ASHRAE minimum LPD allowance for exterior fixtures.
F:K9 |  |  |  |  | For cell K9, input the cut sheet verified wattage for the custom LED fixture.
F:F932 |  |  |  |  | For cell F932, input the description of the custom lighting fixture as corresponds to the submitted cut sheet.
F:K932 |  |  |  |  | For cell K932, input the cut sheet verified wattage of the custom fixture.
F:M932 |  |  |  |  | For cell M932, input the load shape under which the custom fixture type should be evaluated. Only screw-in LEDs and CFLs should be listed as "Screw-in". All other bulb types should be evaluated under the "General" lighting load shape.
3. Use the "Space Type Details" portion of the "General Information" tab to group fixtures into spaces with similar usages, hours of operation, and cooling type. For more detailed information on any of the requirements of the input cells available, or any of the calculated values in this section, select the heading from the full list below, or use the search function in the "Glossary" tab.
G:D38 |  |  |  | Calculation Method | Cell D38, "Calculation Method", is only applicable in the event that the application is for a New Construction project. In this case, specify whether the project should be evaluated using the "Space-by-Space Method" or the "Building Area Method".
G:C42 |  |  |  | Space Designation | For cells C42 through C61, "Space Designation", provide a name for the space described in the details of subsequent columns.
G:D42 |  |  |  | Space Type | For cells D42 through D61, "Space Type", select the option from the drop-down menu that best describes the usage of the designated space type. These space types will be the only spaces available on the lighting inventory sheet, so be sure to include all spaces included in the project.
G:J42 |  |  |  | Schedule | For cells J42 through J61, "Schedule", which schedule will be used to evaluate this space type. The user can either select to use TRM-deemed values, or a custom schedule as created in the table below. Note that in the event of custom schedules, the user will need to create the custom schedules in step 4 before they are available for selection in step 3.
G:N42 |  |  |  | Cooling Type | For cells N42 through N61, "Cooling Type", select the option from the drop-down menu that best describes the cooling type of the designated space type.
G:O42 |  |  |  | Heating Fuel Type | For cells O42 through O61, "Heating Fuel Type", select the option from the drop-down menu that best describes the heating fuel type of the designated space type.
G:P42 |  |  |  | Qty. of Units | For cells P42 through P61, "Qty. of Units", specify the number of units (defined in column Q) included in the designated space type.
G:R42 |  |  |  | Units | Cells R42 through R61, "Units", display the ASHRAE designated units for calculating wattage allowance for the space type selected.
G:U42 |  |  |  | Wattage Allowance Per Unit | Cells U42 through U61, "Wattage Allowance per Unit", display the ASHRAE designated allowable wattage per the unit described in column Q for calculating wattage allowance for the space type selected.
G:O38 |  |  |  | Allowable Watts | Cell O38, "Allowable Watts", displays the ASHRAE allowable total wattage for the facility based on the space details provided.
G:X42 |  |  |  | Atrium Height | Cells X42 through X61, "Atrium Height", for atrium space types enter the height of the atrium in feet.
4. Use the "Custom Lighting Operation Schedules" portion of the "General Information" tab to create custom HOU and CF assumptions in the event that the TRM-deemed values are not a good fit. For more detailed information on any of the requirements of the input cells available, or any of the calculated values in this section, select the heading from the full list below, or use the search function in the "Glossary" tab.
G:S15 |  |  |  | Schedule Designation | For cells R15 through AD15, "Schedule Designation", specify a name for the custom schedule being designated in the cells below.
G:S17 |  |  |  | On | Each row in the "On" column represents the time at which the lights are turned on for the specified scheduled during the specified day of the week. The time should be entered in 24-hr. format.
G:T17 |  |  |  | Off | Each row in the "Off" column represents the time at which the lights are turned off for the specified scheduled during the specified day of the week. The time should be entered in 24-hr. format.
G:S27 |  |  |  | Hours of Use | Each "Hours of Use" cell calculates the annual hours of use associated with the custom schedule input in the cells above. As the formula for calculating Hours of Use in this fashion is hours*day*weeks, and (24)* (7) * (52) does NOT equal 8,760, the HOU includes an adjustment factor to appropriately annualize the usage based on this calculation method.
G:S28 |  |  |  | Coincidence Factor | Each "Coincidence Factor" cell calculates the percentage of the designated peak hours that the lights will be operational according to the custom schedule input in the cells above. Intermediate calculations for this cell can be found starting in row 57.
G:AG27 |  |  |  | Screw-In HOU | Cell AF27, "Screw-In Hours of Use", displays the TRM-deemed hours of use associated with screw-in bulbs for the building type selected.
G:AG28 |  |  |  | Screw-In CF | Cell AF28, "Screw-In CF", displays the TRM-deemed coincidence factor associated with screw-in bulbs for the building type selected.
G:AH27 |  |  |  | General HOU | Cell AG27, "General Hours of Use", displays the TRM-deemed hours of use associated with general service bulbs for the building type selected.
G:AH28 |  |  |  | General CF | Cell AG28, "General Coincidence Factor", displays the TRM-deemed coincidence factor associated with general service bulbs for the building type selected.
G:S24 |  |  |  | Holidays Observed Annually | For each "Holidays Observed Annually" cell, specify the number of days the facility shuts down completely for the given schedule.
G:S25 |  |  |  | Yearly Operating Weeks | For each "Yearly Operating Weeks" cell, specify the number of weeks the facility operates at the given custom schedule.
G:S26 |  |  |  | Unoccupied Peak Weeks | For each "Unoccupied Peak Weeks" cell, specify the number of weeks the facility is closed during the months of June, July, and August for the given custom schedule.
5. Once all information has been input into the "General Information" tab, move onto the "Lighting Inventory" tab.
|  | a) | Complete the orange cells for each line item. Each line item represents fixtures in a discrete area sharing a common baseline fixture, retrofit fixture, controls type, hours of use, coincidence factor, and space cooling type. Fixtures with different entries for any of these categories must be on separate lines. Each line entry must be definitive enough to allow verification of fixture counts in well delineated and discrete areas.
L:C1 |  | b) | For Column C, "Space Type", select the space designation previously defined on the "General Information" tab where the specified fixtures where be installed. This will auto-populate the corresponding IFenergy and IFdemand values in Columns V and W. Only space types previously defined on the "General Information" tab will be available for selection in Column C.
L:D1 |  | c) | Column D, "Space Details", is optional and can be used to differentiate different zones within previously defined space types in the event that multiple line items are present for a single space type.
L:E1 |  | d) | For Column E, "Fixture Code", input the appropriate fixture code found in the "Fixture Identities" tab that most accurately represents the pre-retrofit fixture in question. The "Fixture Identities" tab can be filtered by fixture code, lighting category, subcategory, lamp code, description, ballast type, tube length (for linear fluorescents), lamp quantity, lamp wattage, fixture wattage, code-required baseline fixture, and HOU type for easily locating the appropriate fixture. If a fixture code is not listed in the "Fixture Identities" list, custom cut sheets can be input starting at row 932 of the "Fixture Identities" sheet. Custom cut sheets must be accompanied by a manufacturer's specification sheet for wattage confirmation. Fixture code selection in Column E of the "Lighting Inventory" tab will auto-populate the corresponding Fixture Wattage, Baseline Fixture Code, and Baseline Fixture Wattage in Columns F, J, and K. Column E will not be available for input in the event that this is a new construction project.
L:G1 |  | e) | For Column G, "Fixture Qty.", input the quantity of fixtures removed. This will auto-populate the line item wattage and baseline line item wattage in Columns H and L. Column G will not be available for input in the event that this is a new construction project.
L:I1 |  | f) | For Column I, "Control Type", input the control strategy code that best describes the lighting control strategy employed prior to commencement of the project. This will auto-populate the SVGbase value in Column AC. Column I will not be available for input in the event that this is a new construction project. Controls supported by this tool include:
1. S_LS - Light Switch for Switch Strategy
2. O_OS - Occupancy Sensors for Occupancy Strategy
3. O_TC - Time Clocks for Occupancy Strategy
4. O_EMS - Energy Management System for Occupancy Strategy
5. DL_PS - Photosensors for Daylighting Strategy
6. DL_TC - Time Clocks for Daylighting Strategy
7. PT_DIM - Dimmers for Personal Tuning Strategy
8. PT_WS - Wireless on-off switches for Personal Tuning Strategy
9. PT_BLS - Bi-level switches for Personal Tuning Strategy
10. PT_CC - Computer based controls for Personal Tuning Strategy
11. PT_PSS - Pre-set scene selection for Personal Tuning Strategy
12. IT_DIM - Dimmable ballasts for Institutional Tuning Strategy
13. IT_DIM - On-off or dimmer switches for Institutional Tuning Strategy
14. MT - Multiple Types (Occupancy and personal; tuning/daylighting and other combinations)
L:M1 |  | g) | For Column M, "Fixture Code", input the appropriate fixture code found in the "Fixture Identities" tab that most accurately represents the post-retrofit fixture in question. The "Fixture Identities" tab can be filtered by fixture code, lighting category, subcategory, lamp code, description, ballast type, tube length (for linear fluorescents), lamp quantity, lamp wattage, fixture wattage, code-required baseline fixture, and HOU type for easily locating the appropriate fixture. If a fixture code is not listed in the "Fixture Identities" list, custom cut sheets can be input starting at row 922 of the "Fixture Identities" sheet. Custom cut sheets must be accompanied by a manufacturer's specification sheet for wattage confirmation. Fixture code selection in Column M of the "Lighting Inventory" tab will auto-populate the corresponding Fixture Wattage in Column P.
L:O1 |  | h) | Column O, "Fixture Tag or ID", is optional and can be used to link fixtures to invoices or fixture codes on a fixture schedule of supplemental drawings or plans.
L:Q1 |  | i) | For Column Q, "Fixture Qty.", input the quantity of fixtures installed. This will auto-populate the line item wattage in Column R.
L:S1 |  | j) | For Column S, "Control Type", input the control strategy code that best describes the lighting control strategy employed after the completion of the project. This will auto-populate the SVGbase value in Column AC.
|  | k) | Repeat steps a through j to complete each line. For further clarification on a specific field or column, please see the "Glossary" sheet or consult the TRM. If additional assistance is required, please contact the program manager.
IV. GENERAL NOTE
It is worth noting that magnetic ballasts cannot be manufactured after July 1, 2010 based on the Energy Policy and Conservation Act of 2000. This makes assumptions as to future savings and the Total Resource Cost of the retrofit unclear.
V. DISCLAIMER
This tool allows for custom entries for several fields. This document does not modify any requirements of the PA TRM. If any discrepancy between the TRM and this document exist, the TRM should be followed.
L:F1 |  |  | Column F, "Fixture Wattage", displays the TRM-deemed wattage matching the selected fixture code for the pre-retrofit fixture. This field is only available for retrofit applications.
L:H1 |  |  | Column H, "Line Item Wattage", diplays the total wattage of the pre-retrofit scenario for the full quantity of fixture presented on the corresponding line. This field is only available for retrofit applications.
L:J1 |  |  | Column J, "Fixture Code", diplays the baseline fixture code linked to the pre-retrofit fixture code to which the installed fixtures will be compared. The baseline codes for comparison are dictated by EPACT 2005 and EISA 2007 standards. This field is only available for retrofit applications.
L:K1 |  |  | For retrofit applications, Column K, "Fixture Wattage", displays the TRM-deemed wattage matching the appropriate baseline fixture code for the pre-retrofit fixture. For new construction applications, Column K, "Allowable LPD", displays the ASHRAE designated allowable LPD for the line item provided.
L:L1 |  |  | For retrofit applications, Column L, "Line Item Wattage", displays the total wattage of the baseline scenario for the full quantity of fixture presented on the corresponding line. For new construction applications, Column L, "Allowable Watts", displays the ASHRAE allowable total wattage for the line item based on the space details provided.
L:N1 |  |  | Column N, "HOU Type", displays the load shape corresponding to the fixture type selected. The load shape will be either "General Service Lighting" or "Screw-in".
L:P1 |  |  | Column P, "Fixture Wattage", displays the TRM-deemed wattage matching the selected fixture code for the as-built fixture.
L:R1 |  |  | Column R, "Line Item Wattage", displays the total wattage of the as-built scenario for the full quantity of fixture presented on the corresponding line.
L:T1 |  |  | Column T, "HOU", displays the appropriate hours of use to be used for the line item based on the fixture code and schedule inputs.
L:U1 |  |  | Column U, "CF", displays the appropriate coincidence factor to be used for the line item based on the fixture code and schedule inputs.
L:V1 |  |  | Column V, "Ifenergy", diplays the appropriate energy interactive factor to be used for the line item based on the space type and cooling details.
L:W1 |  |  | Column W, "Ifdemand", displays the appropriate demand interactive factor to be used for the line item based on the space type and cooling details.
L:X1 |  |  | Column X, "SVGbase", displays the appropriate baseline savings factor associated with pre-retrofit controls to be used for the line item based on the control type selection. For new construction, this value is a factor of the percentage of area required by code to have sensors.
L:Y1 |  |  | Column Y, "SVGee", displays the appropriate as-built savings factor associated with as-built controls to be used for the line item based on the control type selection.
L:Z1 |  |  | Column Z, "Δ Load", presents the difference in installed watts between the pre-installation and post-installation lighting scenarios separate from the change in control strategies due to the line item details.
L:AA |  |  | Column AA, "Peak Demand", presents the fraction of connected load reduction (associated with the lighting only) expected to be coincident with the PJM peak demand period due to the line item details.
L:AB |  |  | Column AB, "Energy", presents the total annual energy saved by the lighting improvement separate from the change in control strategies due to the line item details.
L:AC |  |  | Column AC, "Peak Demand", presents the fraction of connected load reduction (associated with the controls only) expected to be coincident with the PJM peak demand period due to the line item details.
L:AD |  |  | Column AD, "Energy", presents the total annual energy saved by the change in control strategies due to the line item details.
L:AE |  |  | Column AE, "Peak Demand", presents the summation of the lighting and controls peak demand savings for the line item.
L:AF |  |  | Column AF, "Energy", presents the summation of the lighting and controls energy savings for the line item.
For cell K9, input the cut sheet verified wattage for the custom LED fixture.

## Changelog
2021 TRM Appendix C: Lighting Audit & Design Tool for Commercial and Industrial Projects
CHANGELOG
Version 12 (Effective June 3, 2010)
1) | Released with TRM Order in June 2010
Version 13 (Submitted October 27, 2010. Effective June 1, 2011)
1) | Created Changelog
2) | Revised "Manual" and "Glossary" to improve user guide and increase usability
3) | Revised "Manual" and "Glossary" to reflect new changes to the TRM
4) | Added Stipulated Usage Group EFLH Table in the "User Input" sheet
5) | Added new building types with corresponding EFLH and CF values
6) | Combined "Wattage Table" and "Extension Table" into one sheet (see column I of the Wattage Table)
7) | Revised fixtures codes and descriptions in Standard Wattage Table
8) | Renamed "Fixture Code Generator" to "Fixture Code Locator" and corrected some programming glitches
Version 14 (Submitted January 19, 2011. Effective June 1, 2011)
1) | In "Manual", section 7.B, the threshold was corrected to 10%, not 15%
2) | In "User Input", Table 5 was revised to reflect TRM Table 3-2
3) | In "User Input", added note to list source for Tables 3 and 5
4) | In "Glossary", added definitions for "pre-installation" and "post-installation"
5) | In "Lighting Form", the EFLH table was updated to reflect TRM Table 3-5
Version 15 (Submitted September 13, 2011 for 2012 Tentative Order)
1) | Global change, replaced all instances of EFLH with HOU
2) | In "User Input", removed old Table 5 to eliminate stipulated hours for usage groups.
3) | In "User Input", added Table 3 to allow custom SVG factor input
Version 16 (Submitted December 4, 2011 for 2012 Final Order)
1) | In "Manual", updated language regarding usage groups.
2) | In "Glossary", removed all references to the old 50 kW threshold.
3) | In "Lighting Form", updated the HOU table to reflect the 2012 TRM (Table 3-4).
4) | In "User Input", added column for custom CF for each usage group.
Version 17 (Submitted August 31, 2012 for 2013 Tentative Order)
1) | In "Lighting Form", updated HOU and CF values lookup table to reflect the 2013 TRM table.
2) | In "Lighting Form", added new building types with corresponding EFLH and CF values to reflect the 2013 TRM table.
3) | In "Lighting Form", updated Control Technologies and Savings Factors values lookup table to reflect 2013 TRM table.
4) | Revised "Manual" and "Glossary" to reflect new changes to the 2013 TRM
Version 18 (Submitted December 3, 2012 for 2013 Final Order)
1) | Revised "Manual" to reflect new changes to the 2013 TRM
Version 19 (Submitted August 29, 2013 for 2014 Tentative Order)
1) | Created "Fixtures Form" and "Controls Form" to calculate energy and peak demand savings for lighting fixtures and controls measures separately to be consistent with TRM protocols.
Created separate tabs for "Fixtures User Input" and "Controls User Input" for user input options
2) | Added new fixture codes in the "Wattage Table" (cells 157 to 178 and cells 651 to 669)
3) | Revised "Manual" and "Glossary" to reflect new changes to the TRM and Appendix C
Version 20 (Submitted December 05, 2013 for 2014 Final Order)
1) | Updated "Fixture Code Locator" to be compatible with Pulse-Start Metal Halide entries.
2) | Updated header fields on "Lighting Controls Form" to create autonomy between Lighting Controls and Fixture information.
3) | Revised "Fixture Code Legend" to reflect new changes to the TRM and Appendix C.
4) | Revised "Manual" and "Glossary" to reflect new changes to the TRM and Appendix C.
5) | Updated energy and peak demand savings algorithms in the Fixtures Form tab.
Version 21 (Submitted August 21, 2014 for 2015 Tentative Order)
1) | Updated Wattage Table for additional fixtures.
2) | Included LED Traffic and Pedestrian Signal Upgrades in the Prescriptive Table (values inserted in cells directly rather than pulled from "Wattage Table").
3) | Updated "Maunal" hyperlinks to match worksheet titles and made all hyperlinks functional.
4) | Cleaned up "Glossary" to ensure all cell and column references match.
Version 22 (Submitted March 16, 2015 for 2016 Tentative Order)
1) | Overhauled setup, formatting, and interface for enhanced usability.
2) | Included "key" describing which cells are available for input and which should not be changed.
3) | Updated tool to be compatible with "New Construction" as well as "Retrofit" projects.
4) | Updated tool to be compatible with custom operating schedules.
5) | Combined controls and fixtures inputs into one tab.
6) | Added functionality to compare installed fixtures to code required baseline.
7) | Revised HOU, CF, and IF assumptions to reflect new changes to the TRM.
8) | Revised "Wattage Table", now called "Fixture Identities", to reflect new changes to the TRM and Appendix C.
9) | Transformed "Glossary" into a searchable database for easier navigation.
10) | Revised "Manual" and "Glossary" to reflect new changes to the TRM and Appendix C.
Version 23 (Submitted March 10, 2017 for 2016 TRM Errata corrections)
1) | Cells R28:AD28 (Lighting Operation Schedule section) have been corrected to enable accurate coincidence factor calculations for custom schedule designations.
2) | Data validation for array Fixture Identities F9:F28 (Description) has been changed to reference Lookups V9:V15 (formerly V9:V14), where a "Custom" option was added to the array along with a corresponding Fixture Code of "C."
3) | Range Name "LED_Codes" has been extended by 1 row to include Lookups V15:X15
4) | HOU Type was converted to a user-defined field by adding Data Validation criteria to array Fixture Identities M9:M28, enabling user to select General or Screw-In (mirroring the inputs for other custom fixtures near the bottom of the Fixture Identities worksheet)
5) | Data Validation criteria for array Fixture Identities K9:K28 was changed from Whole Number to Decimal to enable non-integer fixture wattages
6) | Cell P35 on the Lookups worksheet has been changed from “Miscellaneous” to “Miscellaneous / Other”
7) | Cell P25 on Lookups has been changed to Building Type (from Control Type)
8) | Capabilities for user-defined/custom SVGbase (new construction) and SVG ee (controls) inputs have been added to the tool by appending the lookup arrays and adding a column for custom facility types to the Lighting Inventory worksheet. Data validation rules on the Lighting Inventory worksheet have been updated accordingly.
9) | Non-Integral Ballast LED Fixture Codes table (Lookups) renamed to LED Code Builder
10) | Cell D21 on Summary worksheet has been changed to sum the two cells above (lighting and controls), rather than summing only the lighting savings (note that cell E21 does not include controls because connected load is not impacted by controls).
See PA PUC Secretarial Letter Re: Technical Reference Manual 2016 errata for additional context and related TRM changes
Version 24 (Submitted June 28, 2019 for 2021 Final Order)
1) | Adjusted custom hours of use and coincidence factor module to accommodate dusk-to-dawn lighting.
2) | Made active link on "Lighting Inventory" tab to configure custom SVG values.
3) | Decremented baseline incandescent lamp wattages for non-specialty lamps to be in compliance with EISA.
4) | Corrected error in which columns J, K, and L of the "Lighting Inventory" tab did not populate for new construction projects utilizing "Whole Building Method".
5) | Added 36" and 96" linear LED options to the LED Fixture Builder. Updated "Tube Length" calculation on the "Fixture Identities" sheet to properly report lengths for 36" and 96" lamps.
6) | Expanded functionality to allow for multiple deemed space types (i.e. interior, exterior, refrigeration, and exit). This is facilitated by using either the "Deemed" or "Mixed" modes in General Information cell I26.
7) | Adjusted LPD baseline values to be consistent with IECC 2015 as sourced from https://codes.iccsafe.org/public/document/IECC2015/chapter-4-ce-commercial-energy-efficiency.
8) | Adjusted energy savings algorithm to ignore baseline SVG factor in the event that both the pre-retrofit and post-retrofit cases both employ either method of Daylighting controls. This adjustment was made in order to correct the issue through which known photocell operating hours were further discounted by the Photocell SVG factor.
9) | Revised "Manual" and "Glossary" to reflect new changes to the TRM and Appendix C.
10) | Revised "Glossary" sheet to reflect correct name of "Fixture Identities" sheet.
11) | Revised and expanded "LED_Codes" named range to include LED Linear Fluorescent Tube Replacement "Type" in the Description. Revised "Code" for same fixtures to append Type to the end of the Code (i.e., LTA, LTB, LTC).
12) | Revised Screw-Based CFL & LED/Other General Service Lighting Exterior and Parking Garage HOU for consistency with new TRM.
13) | Revised New Construction SVG Accountability "% Req." assumptions for consistency with IECC 2015.
14) | Added "Small Business Direct Install" input on the "General Information" worksheet. When "Yes" is selected, the T12 baseline adjustment will be disabled.
15) | Added data validation to "Space Designation" on the "General Information" sheet to prevent duplicate entry.
16) | Corrected TRM-based HOU/CF/IF for street lighting "Facility Type." If "Street Lighting" is the selected facility, "Schedule" and "Cooling Type" choices are limited appropriately.
17) | Expanded "LED_Codes" to include "Troffer LED Panel"
18) | Corrected functionality for New Construction exterior lighting projects. Tool now properly populates appropriate baseline requirements.
19) | Added "Exterior, Photocell-Controlled" facility type with dusk-to-dawn operating hours.
20) | Added additional input for Atrium space types to capture atrium height. This is required to determine New Construction LPD requirement.
21) | Revised tool to require "Heating Fuel Type" at the space type-level. Tool now accommodates multiple heating fuel types within a single project.

## Glossary
2021 TRM Appendix C: Lighting Audit & Design Tool for Commercial and Industrial Projects
GLOSSARY
Not sure what to put into a certain cell? Let us help you! Search by tab name and cell number, or use the filtering function on the table below to find the cell in question.
Tab Name: |  |  | Instructions:
| General Information | G:D13 | For cell D13, "Applicant Name", specify the name of the applicant as corroborated by the submitted W9.
Cell Reference (i.e. G13):
D13
Tab |  | Cell | Field Type | Heading | Description | Availability
General Information |  | D13 | Input Field | Applicant Name | The name of the applicant as corroborated by the submitted W9. | -
General Information |  | D14 | Input Field | Facility Name | A name of the facility for reference in the event that the applicant will be submitting applications for multiple facilities within one program year. | -
General Information |  | D16 | Input Field | Address | The address at which the project takes place. | -
General Information |  | D17 | Input Field | City | The city in which the facility is located. | -
General Information |  | H17 | Input Field | State | The state in which the facility is located. | -
General Information |  | J17 | Input Field | Zip | The zip code in which the facility is located. | -
General Information |  | D18 | Input Field | Utility | The electric distribution company who services the facility. | -
General Information |  | H18 | Input Field | Account No. | The account number on record with electric distributing company. If this is a pre-application for a new construction project, and service has not yet been connect, input "TBD". | -
General Information |  | D19 | Input Field | Contact Name and Title | The person who should be contacted in the event that there are any questions regarding this application. | -
General Information |  | D20 | Input Field | Phone | The phone number where the designated contact can be reached. | -
General Information |  | D21 | Input Field | Email | The email address where the designated contact can be reached. | -
General Information |  | D23 | Input Field | Facility Type | The Facility Type that best describes the usage of the facility. | -
General Information |  | D24 | Input Field | Construction Type | The type of project, whether it is a retrofit or new construction. | -
General Information |  | D25 | Input Field | Facility Size | The total square footage of the facility at which the project occurs. This field is optional for retrofit applications. | Only if "New Construction" is selected as the construction type in Cell D24.
General Information |  | D26 | Input Field | Installation Date | The completion (or expected completion) date of the project. | -
General Information |  | I26 | Input Field | HOU/CF Source | The preferred source of HOU and CF assumptions. Note that if "Deemed" is selected, the calculator will assume a single designated Facilty Type for determining hours of use and coincidence factors. | -
General Information |  | I27 | Input Field | Is this a Small Business Direct Install Project? | Indicate whether or not this is a small business direct install project. Selecting "Yes" will disable the T12 baseline adjustment feature. | -
General Information |  | I29 | Input Field | Which exterior lighting zone describes your project? | The ASHRAE exterior lighting zone associated with the facility for New Construction LPD calculations. This cell is only available for input if this is a new construction project. | Only if "New Construction" is selected as the construction type in Cell D24.
General Information |  | D38 | Input Field | Calculation Method | The ASHRAE evaluation method for New Construction projects that should be used for this project. This cell is only available for input if this is a new construction project. | Only if "New Construction" is selected as the construction type in Cell D24.
General Information |  | C42 | Input Field | Space Designation | The user-defined name of the space that will be defined in the subsequent columns. | -
General Information |  | D42 | Input Field | Space Type | The ASHRAE Space Type that best describes the usage of the space. These space types will be the only spaces available on the lighting inventory sheet, so be sure to include all spaces included in the project. | Only if "New Construction" is selected as the construction type in Cell D24.
General Information |  | J42 | Input Field | Schedule | The schedule that corresponds to the selected space type. Note that in the event of custom schedules, the user will need to create the custom schedules in step 5 before they are available for selection in step 4. | -
General Information |  | N42 | Input Field | Cooling Type | The type of cooling employed in the selected space type. | -
General Information |  | O42 | Input Field | Heating Fuel Type | The heating fuel source in the selected space type. | -
General Information |  | P42 | Input Field | Qty. of Units | For cells P41 through P60, "Qty. of Units", specify the number of units (described in column R) included in the designated space type. | Only if "New Construction" is selected as the construction type in Cell D24.
General Information |  | R42 | Calculated Value | Units | The ASHRAE designated units for which an allowable wattage is specified for the space type selected. | Only if "New Construction" is selected as the construction type in Cell D24.
General Information |  | U42 | Calculated Value | Wattage Allowance Per Unit | The ASHRAE designated allowable wattager per the unit specified for the space type selected. This will be used as the baseline for savings calculations in the event that this is a New Construction project. | Only if "New Construction" is selected as the construction type in Cell D24.
General Information |  | X42 | Input Field | Atrium Height | For atrium space types, the height of the atrium in feet. | Only if "New Construction" is selected as the construction type in Cell D24 and Space Designation is "Atrium, < 40 ft. in height" or "Atrium, >= 40 ft. in height."
General Information |  | O38 | Calculated Value | Allowable Watts | The ASHRAE allowable total wattage for the facility based on the space details provided. | Only if "New Construction" is selected as the construction type in Cell D24.
General Information |  | R15 | Input Field | Schedule Designation | The name for the custom schedule being designated in the cells below. | Only if "Deemed" is selected as the HOU/CF Source in Cell I26.
General Information |  | R17 | Input Field | On | The time at which the lights are turned on for the specified scheduled during the specified day of the week. The time should be entered in 24-hr. format. | Only if "Deemed" is selected as the HOU/CF Source in Cell I26.
General Information |  | S17 | Input Field | Off | The time at which the lights are turned off for the specified scheduled during the specified day of the week. The time should be entered in 24-hr. format. For overnight hours of use, add 24 to the ending time (i.e. if the facility is a restaurant that closes at 3AM, the ending time will be 27). | Only if "Deemed" is selected as the HOU/CF Source in Cell I26.
General Information |  | S27 | Calculated Value | Hours of Use | The annual hours of use associated with the custom schedule input in the cells above. As the formula for calculating Hours of Use in this fashion is hours*day*weeks, and (24)* (7) * (52) does NOT equal 8,760, the HOU includes an adjustment factor to appropriately annualize the usage based on this calculation method. | -
General Information |  | S28 | Calculated Value | Coincidence Factor | The percentage of the designated peak hours that the lights will be operational according to the custom schedule input in the cells above. Intermediate calculations for this cell can be found starting in row 57. | -
General Information |  | AG27 | Calculated Value | Screw-In HOU | The TRM-deemed hours of use associated with screw-in bulbs for the building type selected. | -
General Information |  | AG28 | Calculated Value | Screw-In CF | The TRM-deemed coincidence factor associated with screw-in bulbs for the building type selected. | -
General Information |  | AH27 | Calculated Value | General HOU | The TRM-deemed hours of use associated with general service bulbs for the building type selected. | -
General Information |  | AH28 | Calculated Value | General CF | The TRM-deemed coincidence factor associated with general service bulbs for the building type selected. | -
General Information |  | S24 | Input Field | Holidays Observed Annually | The number of days the facility shuts down completely. | Only if "Deemed" is selected as the HOU/CF Source in Cell I26.
General Information |  | S25 | Input Field | Yearly Operating Weeks | The number of weeks the facility operates at the custom schedules provided. | Only if "Deemed" is selected as the HOU/CF Source in Cell I26.
General Information |  | S26 | Input Field | Unoccupied Peak Weeks | The number of weeks the facility is unoccupied during the months of June, July, and Augsust. | Only if "Yearly Operating Weeks" is less than 52 in Cell V28.
Lighting Inventory |  | C13 | Input Field | Space Designation | The space type previously defined on the "General Information" tab where the specified fixtures where be installed. Only space types previously defined on the "General Information" tab will be available for selection in Column C. | -
Lighting Inventory |  | D13 | Input Field | Space Details | The specified details used to delineate fixture types within the same space type. | -
Lighting Inventory |  | E13 | Input Field | Fixture Code (Pre) | The appropriate fixture code found in the "Fixture Search" tab that most accurately represents the pre-retrofit fixture in question. | Only if "Retrofit" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | F13 | Calculated Value | Fixture Wattage (Pre) | The TRM-deemed wattage matching the selected fixture code for the pre-retrofit fixture. | Only if "Retrofit" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | G13 | Input Field | Fixture Quantity (Pre) | The quantity of fixtures removed as part of the retrofit. | Only if "Retrofit" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | H13 | Calculated Value | Line Item Wattage (Pre) | The total wattage of the pre-retrofit scenario for the full quantity of fixture presented on the corresponding line. | Only if "Retrofit" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | I13 | Input Field | Control Type (Pre) | The control technology utilized in the pre-installation case. | Only if "Retrofit" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | J13 | Calculated Value | Fixture Code (Baseline) | The code-required baseline fixture code linked to the pre-retrofit fixture code to which the installed fixtures will be compared. | Only if "Retrofit" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | K13 | Calculated Value | Fixture Wattage (Baseline) | The TRM-deemed wattage matching the appropriate baseline fixture code for the pre-retrofit fixture. | Only if "Retrofit" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | K13 | Calculated Value | Allowable LPD | The ASHRAE designated allowable LPD for the line item provided. This will be used as the baseline for savings calculations in the event that this is a New Construction project. | Only if "New Construction" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | L13 | Calculated Value | Line Item Wattage (Baseline) | The total wattage of the baseline scenario for the full quantity of fixture presented on the corresponding line. | Only if "Retrofit" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | L13 | Calculated Value | Allowable Power | The ASHRAE allowable total wattage for the line item based on the space details provided. | Only if "New Construction" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | M13 | Input Field | Fixture Code (Post) | The appropriate fixture code found in the "Fixture Search" tab that most accurately represents the post-construction fixture in question. | -
Lighting Inventory |  | N13 | Calculated Value | HOU Type | The load shape corresponding to the fixture type selected. | -
Lighting Inventory |  | O13 | Input Field | Fixture Tag or ID | The fixture designation presented on either the invoices or supplemental plans. | -
Lighting Inventory |  | P13 | Calculated Value | Fixture Wattage (Post) | The TRM-deemed wattage matching the selected fixture code for the as-built fixture. | -
Lighting Inventory |  | Q13 | Input Field | Fixture Quantity. (Post) | The quantity of fixtures removed as part of the project. | -
Lighting Inventory |  | R13 | Calculated Value | Line Item Wattage (Post) | The total wattage of the as-built scenario for the full quantity of fixture presented on the corresponding line. | -
Lighting Inventory |  | S13 | Input Field | Control Type (Post) | The control technology utilized in the as-built case. | -
Lighting Inventory |  | T13 | Calculated Value | HOU | The appropriate hours of use to be used for the line item based on the fixture code and schedule inputs. | -
Lighting Inventory |  | U13 | Calculated Value | CF | The appropriate coincidence factor to be used for the line item based on the fixture code and schedule inputs. | -
Lighting Inventory |  | V13 | Calculated Value | IFenergy | The appropriate energy interactive factor to be used for the line item based on the space type and cooling details. | -
Lighting Inventory |  | W13 | Calculated Value | IFdemand | The appropriate demand interactive factor to be used for the line item based on the space type and cooling details. | -
Lighting Inventory |  | X13 | Calculated Value | SVGbase | The appropriate baseline savings factor associated with pre-retrofit controls to be used for the line item based on the control type selection. For new construction, this value is a factor of the percentage of area required by code to have sensors. | -
Lighting Inventory |  | Y13 | Calculated Value | SVGee | The appropriate as-built savings factor associated with as-built controls to be used for the line item based on the control type selection. | -
Lighting Inventory |  | Z13 | Calculated Value | Δ Load (Lighting) | The difference in installed watts between the pre-installation and post-installation lighting scenarios separate from the change in control strategies due to the line item details. | Only if "Retrofit" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | AA13 | Calculated Value | Peak Demand (Lighting) | The fraction of connected load reduction (associated with the lighting only) expected to be coincident with the PJM peak demand period due to the line item details. | Only if "Retrofit" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | AB13 | Calculated Value | Energy (Lighting) | The total annual energy saved by the lighting improvement separate from the change in control strategies due to the line item details. | Only if "Retrofit" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | AC13 | Calculated Value | Peak Demand (Controls) | The fraction of connected load reduction (associated with the controls only) expected to be coincident with the PJM peak demand period due to the line item details. | Only if "Retrofit" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | AD13 | Calculated Value | Energy (Controls) | The total annual energy saved by the change in control strategies due to the line item details. | Only if "Retrofit" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | AE13 | Calculated Value | Peak Demand (Total) | The summation of the lighting and controls peak demand savings for the line item. | Only if "Retrofit" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | AF13 | Calculated Value | Energy (Total) | The summation of the lighting and controls energy savings for the line item. | Only if "Retrofit" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | Z7 | Calculated Value | Summary: Δ Load (Lighting) | The summation of the change in connected lighting load of all line items. | -
Lighting Inventory |  | AA7 | Calculated Value | Summary: Peak Demand (Lighting) | The summation of the peak demand savings due to lighting only of all line items. | -
Lighting Inventory |  | AB7 | Calculated Value | Summary: Energy (Lighting) | The summation of the energy savings due to lighting only of all line items. | -
Lighting Inventory |  | AC7 | Calculated Value | Summary: Peak Demand (Controls) | The summation of the peak demand savings due to controls only of all line items. | -
Lighting Inventory |  | AD7 | Calculated Value | Summary: Energy (Controls) | The summation of the energy savings due to controls only of all line items. | -
Lighting Inventory |  | AE7 | Calculated Value | Summary: Peak Demand (Total) | The summation of the total peak demand savings associated with both lighting and controls upgrades for all line items. | -
Lighting Inventory |  | AF7 | Calculated Value | Summary: Energy (Total) | The summation of the total energy savings associated with both lighting and controls upgrades for all line items. | -
Fixture Identities |  | K9 | Input Field | Watts per Fixture | The cut sheet verified wattage for the custom LED fixture. | -
Fixture Identities |  | F932 | Input Field | Description | The description of the custom lighting fixture as corresponds to the submitted cut sheet. | -
Fixture Identities |  | K932 | Input Field | Watts per Fixture | The cut sheet verified wattage of the custom fixture. | -
Fixture Identities |  | M932 | Input Field | HOU Type | The load shape under which the custom fixture type should be evaluated. | -

## General Information
2021 TRM Appendix C: Lighting Audit & Design Tool for Commercial and Industrial Projects
GENERAL INFORMATION
| KEY: | Input Field |  |  | Example Cell |  |  | Cell Creating Error in Calculations
|  | Calculated Value |  |  | Intermediate Calc.
❶ Project / Site Information | [7 empty] | ❷ Custom Lighting Operation Schedules
| Provide basic project information below. | [7 empty] | If you have opted to use custom HOU/CF values, you can create up to 6 custom lighting operation schedules for varying space types using the table below. Enter the on/off times of the facility lighting for each day in 24-hr. format. The first column shows an example of a facility that is open from 8AM to 5PM on weekdays, 24 hours on Saturday, and dusk-to-dawn on Sunday for reference.
Applicant Name:
Facility Name:
[10 empty] | Schedule Designation | Example |  | <Input Name> |  | <Input Name> |  | <Input Name> |  | <Input Name> |  |  | <Input Name> |  | <Input Name> |  | TRM
| Installation Address: | [9 empty] | On | Off | On | Off | On | Off | On | Off | On |  | Off | On | Off | On | Off | Screw-In | General
| City: |  |  | State: |  | Zip: |  | (Standard Input Example) |  | Monday | 8 | 17
| Utility: |  | Account No.: | [6 empty] | Tuesday | 8 | 17
| Contact Name & Title: | [8 empty] | Wednesday | 8 | 17
| Phone: | [8 empty] | Thursday | 8 | 17
| Email: | [8 empty] | Friday | 8 | 17
[8 empty] | (24/7 Example) |  | Saturday | 0 | 24
| Facility Type: | [6 empty] | (Dusk-to-Dawn Example) |  | Sunday | 19 | 31
| Construction Type: | [8 empty] | Holidays Observed Annually | 8
| Facility Size (ft2): | [8 empty] | Yearly Operating Weeks | 52
| Installation Date: |  |  |  | HOU/CF Source: |  |  |  |  | Unoccupied Peak Weeks | 0 | [14 empty] | Interior
[5 empty] | Is this a Small Business Direct Install Project? |  |  |  |  | Hours of Use | 4151.5714
[10 empty] | Coincidence Factor | 0.75
❸ Space Type Details | [18 empty] | Intermediate CF Calculations
| Create up to 20 custom space types using the table below. These space types will be used on the "Lighting Inventory" form to describe where fixtures were installed. | [18 empty] | Custom Coincidence Factor Calculations
[23 empty] | 14 | 15 | 16 | 17
| Calculation Method: | Space by Space Method | [5 empty] | Allowable Watts: | 0 | [10 empty] | Monday |  |  | 1 | 1 | 1 | 0 | Example
[15 empty] | Wattage Allowance per Unit |  |  | Atrium Height |  | Tuesday |  |  | 1 | 1 | 1 | 0
| Space Designation | Space Type |  |  |  |  | Schedule | Cooling Type | Heating Fuel Type | Qty. of Units |  | Units | [7 empty] | Wednesday |  |  | 1 | 1 | 1 | 0
| Example | Office - Enclosed |  |  |  |  | Example | Comfort Cooled | Non-Electric | 20000 |  | Square Feet | [5 empty] | Feet |  | Thursday |  |  | 1 | 1 | 1 | 0
| <Name Your Space Type> | [18 empty] | Friday |  |  | 1 | 1 | 1 | 0
| <Name Your Space Type> | [18 empty] | CF |  |  | 0.75
| <Name Your Space Type> | [18 empty] | Monday |  |  | 0 | 0 | 0 | 0 | <Input Name>
| <Name Your Space Type> | [18 empty] | Tuesday |  |  | 0 | 0 | 0 | 0
| <Name Your Space Type> | [18 empty] | Wednesday |  |  | 0 | 0 | 0 | 0
| <Name Your Space Type> | [18 empty] | Thursday |  |  | 0 | 0 | 0 | 0
| <Name Your Space Type> | [18 empty] | Friday |  |  | 0 | 0 | 0 | 0
| <Name Your Space Type> | [18 empty] | CF |  |  | 0
| <Name Your Space Type> | [18 empty] | Monday |  |  | 0 | 0 | 0 | 0 | <Input Name>
| <Name Your Space Type> | [18 empty] | Tuesday |  |  | 0 | 0 | 0 | 0
| <Name Your Space Type> | [18 empty] | Wednesday |  |  | 0 | 0 | 0 | 0
| <Name Your Space Type> | [18 empty] | Thursday |  |  | 0 | 0 | 0 | 0
| <Name Your Space Type> | [18 empty] | Friday |  |  | 0 | 0 | 0 | 0
| <Name Your Space Type> | [18 empty] | CF |  |  | 0
| <Name Your Space Type> | [18 empty] | Monday |  |  | 0 | 0 | 0 | 0 | <Input Name>
| <Name Your Space Type> | [18 empty] | Tuesday |  |  | 0 | 0 | 0 | 0
| <Name Your Space Type> | [18 empty] | Wednesday |  |  | 0 | 0 | 0 | 0
| <Name Your Space Type> | [18 empty] | Thursday |  |  | 0 | 0 | 0 | 0
| <Name Your Space Type> | [18 empty] | Friday |  |  | 0 | 0 | 0 | 0
| <Name Your Space Type> | [18 empty] | CF |  |  | 0
[20 empty] | Monday |  |  | 0 | 0 | 0 | 0 | <Input Name>
[20 empty] | Tuesday |  |  | 0 | 0 | 0 | 0
[20 empty] | Wednesday |  |  | 0 | 0 | 0 | 0
[20 empty] | Thursday |  |  | 0 | 0 | 0 | 0
[20 empty] | Friday |  |  | 0 | 0 | 0 | 0
[20 empty] | CF |  |  | 0
[20 empty] | Monday |  |  | 0 | 0 | 0 | 0 | <Input Name>
[20 empty] | Tuesday |  |  | 0 | 0 | 0 | 0
[20 empty] | Wednesday |  |  | 0 | 0 | 0 | 0
[20 empty] | Thursday |  |  | 0 | 0 | 0 | 0
[20 empty] | Friday |  |  | 0 | 0 | 0 | 0
[20 empty] | CF |  |  | 0
[20 empty] | Monday |  |  | 0 | 0 | 0 | 0 | <Input Name>
[20 empty] | Tuesday |  |  | 0 | 0 | 0 | 0
[20 empty] | Wednesday |  |  | 0 | 0 | 0 | 0
[20 empty] | Thursday |  |  | 0 | 0 | 0 | 0
[20 empty] | Friday |  |  | 0 | 0 | 0 | 0
[20 empty] | CF |  |  | 0

## Lighting Inventory
2021 TRM Appendix C: Lighting Audit & Design Tool for Commercial and Industrial Projects
LIGHTING INVENTORY
[24 empty] | PROJECT SUMMARY |  | Lighting |  |  | Controls |  | Total
|  |  |  | Using Non-Integrated Ballast LED Fixtures? Click here to configure LED fixture codes. |  |  |  |  | Using Custom Cut-Sheet Fixtures? Click here to create custom fixture codes. |  |  |  |  | Using Custom Controls Savings Factors? Click here to create custom SVG values. | [11 empty] | Δ Load (kW) | Peak Demand (kW) | Energy (kWh) | Peak Demand (kW) | Energy (kWh) | Peak Demand (kW) | Energy (kWh)
[26 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
SAVINGS
|  |  |  | PRE-RETROFIT DETAILS |  |  |  |  | BASELINE DETAILS |  |  | POST-INSTALLATION DETAILS | [6 empty] | ASSUMPTIONS | [6 empty] | LIGHTING |  |  | CONTROLS |  | TOTAL
| Line Item | Space Designation | Optional Details (e.g. Room Number or Fixture Make & Model) | Fixture Code | Fixture Wattage | Fixture Quantity | Line Item Wattage | Control Type | Fixture Code | Fixture Wattage | Line Item Wattage | Fixture Code | HOU Type | Fixture Tag or ID (Opt.) | Fixture Wattage | Fixture Quantity | Line Item Wattage | Control Type | HOU | CF | IFenergy | IFdemand | Custom NC Facility Type (optional) | SVGbase | SVGee | Δ Load (kW) | Peak Demand (kW) | Energy (kWh) | Peak Demand (kW) | Energy (kWh) | Peak Demand (kW) | Energy (kWh) | Controls Installed Counter | Lamps Removed Counter | Lamps Installed Counter
| Ex. | Example | Example | F82EHS | 227 | 10 | 2270 | S_LS | F82LHL | 160 | 1600 | F43LL | General | A/A1 | 93 | 10 | 930 | O_OS | 2294 | 0.48 | 0.04 | 0.23 | Custom | 0 | 0.24 | 0.67 | 0.39557 | 1598.4592 | 0.13178 | 532.5016 | 0.52735 | 2130.9608
0 | 1 | [31 empty] | 0 | 0 | 0
0 | 2 | [31 empty] | 0 | 0 | 0
0 | 3 | [31 empty] | 0 | 0 | 0
0 | 4 | [31 empty] | 0 | 0 | 0
0 | 5 | [31 empty] | 0 | 0 | 0
0 | 6 | [31 empty] | 0 | 0 | 0
0 | 7 | [31 empty] | 0 | 0 | 0
0 | 8 | [31 empty] | 0 | 0 | 0
0 | 9 | [31 empty] | 0 | 0 | 0
0 | 10 | [31 empty] | 0 | 0 | 0
0 | 11 | [31 empty] | 0 | 0 | 0
0 | 12 | [31 empty] | 0 | 0 | 0
0 | 13 | [31 empty] | 0 | 0 | 0
0 | 14 | [31 empty] | 0 | 0 | 0
0 | 15 | [31 empty] | 0 | 0 | 0
0 | 16 | [31 empty] | 0 | 0 | 0
0 | 17 | [31 empty] | 0 | 0 | 0
0 | 18 | [31 empty] | 0 | 0 | 0
0 | 19 | [31 empty] | 0 | 0 | 0
0 | 20 | [31 empty] | 0 | 0 | 0
0 | 21 | [31 empty] | 0 | 0 | 0
0 | 22 | [31 empty] | 0 | 0 | 0
0 | 23 | [31 empty] | 0 | 0 | 0
0 | 24 | [31 empty] | 0 | 0 | 0
0 | 25 | [31 empty] | 0 | 0 | 0
0 | 26 | [31 empty] | 0 | 0 | 0
0 | 27 | [31 empty] | 0 | 0 | 0
0 | 28 | [31 empty] | 0 | 0 | 0
0 | 29 | [31 empty] | 0 | 0 | 0
0 | 30 | [31 empty] | 0 | 0 | 0
0 | 31 | [31 empty] | 0 | 0 | 0
0 | 32 | [31 empty] | 0 | 0 | 0
0 | 33 | [31 empty] | 0 | 0 | 0
0 | 34 | [31 empty] | 0 | 0 | 0
0 | 35 | [31 empty] | 0 | 0 | 0
0 | 36 | [31 empty] | 0 | 0 | 0
0 | 37 | [31 empty] | 0 | 0 | 0
0 | 38 | [31 empty] | 0 | 0 | 0
0 | 39 | [31 empty] | 0 | 0 | 0
0 | 40 | [31 empty] | 0 | 0 | 0
0 | 41 | [31 empty] | 0 | 0 | 0
0 | 42 | [31 empty] | 0 | 0 | 0
0 | 43 | [31 empty] | 0 | 0 | 0
0 | 44 | [31 empty] | 0 | 0 | 0
0 | 45 | [31 empty] | 0 | 0 | 0
0 | 46 | [31 empty] | 0 | 0 | 0
0 | 47 | [31 empty] | 0 | 0 | 0
0 | 48 | [31 empty] | 0 | 0 | 0
0 | 49 | [31 empty] | 0 | 0 | 0
0 | 50 | [31 empty] | 0 | 0 | 0
0 | 51 | [31 empty] | 0 | 0 | 0
0 | 52 | [31 empty] | 0 | 0 | 0
0 | 53 | [31 empty] | 0 | 0 | 0
0 | 54 | [31 empty] | 0 | 0 | 0
0 | 55 | [31 empty] | 0 | 0 | 0
0 | 56 | [31 empty] | 0 | 0 | 0
0 | 57 | [31 empty] | 0 | 0 | 0
0 | 58 | [31 empty] | 0 | 0 | 0
0 | 59 | [31 empty] | 0 | 0 | 0
0 | 60 | [31 empty] | 0 | 0 | 0
0 | 61 | [31 empty] | 0 | 0 | 0
0 | 62 | [31 empty] | 0 | 0 | 0
0 | 63 | [31 empty] | 0 | 0 | 0
0 | 64 | [31 empty] | 0 | 0 | 0
0 | 65 | [31 empty] | 0 | 0 | 0
0 | 66 | [31 empty] | 0 | 0 | 0
0 | 67 | [31 empty] | 0 | 0 | 0
0 | 68 | [31 empty] | 0 | 0 | 0
0 | 69 | [31 empty] | 0 | 0 | 0
0 | 70 | [31 empty] | 0 | 0 | 0

## Fixture Identities
2021 TRM Appendix C: Lighting Audit & Design Tool for Commercial and Industrial Projects
FIXTURE SEARCH
Use drop-down arrows in each column heading to filter by parameter. If your application contains non-integrated ballast LED fixtures, the fixtures will need to be configured starting on row 9. If your application contains custom cut-sheet accompanied fixtures, the fixtures will need to be configured starting on row 932. All custom and non-integrated ballast LED fixtures require cut sheets for fixture configuration verification.
Fixture Code | Lighting Category | Subcategory | Lamp Code | Description | Ballast | Tube Length | Lamps Per Fixture | Watts Per Lamp | Watts Per Fixture | Baseline Fixture | HOU Type
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit | Custom LED | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit | Custom LED | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit | Custom LED | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit | Custom LED | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit | Custom LED | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit | Custom LED | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit | Custom LED | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit | Custom LED | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit | Custom LED | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit | Custom LED | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit | Custom LED | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit | Custom LED | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit | Custom LED | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit | Custom LED | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit | Custom LED | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit | Custom LED | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit | Custom LED | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit | Custom LED | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit | Custom LED | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit | Custom LED | Edit
SLED2/1 | LED | LED Screw-In | LED 2W | Screw In - Light Emitting Diode Lamp, (1) 2W | Electronic |  | 1 | 2 | 2 | SLED2/1 | Screw-In
SLED3/1 | LED | LED Screw-In | LED 3W | Screw In - Light Emitting Diode Lamp, (1) 3W | Electronic |  | 1 | 3 | 3 | SLED3/1 | Screw-In
SLED4/1 | LED | LED Screw-In | LED 4W | Screw In - Light Emitting Diode Lamp, (1) 4W | Electronic |  | 1 | 4 | 4 | SLED4/1 | Screw-In
SLED5/1 | LED | LED Screw-In | LED 5W | Screw In - Light Emitting Diode Lamp, (1) 5W | Electronic |  | 1 | 5 | 5 | SLED5/1 | Screw-In
SLED6/1 | LED | LED Screw-In | LED 6W | Screw In - Light Emitting Diode Lamp, (1) 6W | Electronic |  | 1 | 6 | 6 | SLED6/1 | Screw-In
SLED7/1 | LED | LED Screw-In | LED 7W | Screw In - Light Emitting Diode Lamp, (1) 7W | Electronic |  | 1 | 7 | 7 | SLED7/1 | Screw-In
SLED8/1 | LED | LED Screw-In | LED 8W | Screw In - Light Emitting Diode Lamp, (1) 8W | Electronic |  | 1 | 8 | 8 | SLED8/1 | Screw-In
SLED9/1 | LED | LED Screw-In | LED 9W | Screw In - Light Emitting Diode Lamp, (1) 9W | Electronic |  | 1 | 9 | 9 | SLED9/1 | Screw-In
SLED10/1 | LED | LED Screw-In | LED 10W | Screw In - Light Emitting Diode Lamp, (1) 10W | Electronic |  | 1 | 10 | 10 | SLED10/1 | Screw-In
SLED11/1 | LED | LED Screw-In | LED 11W | Screw In - Light Emitting Diode Lamp, (1) 11W | Electronic |  | 1 | 11 | 11 | SLED11/1 | Screw-In
SLED12/1 | LED | LED Screw-In | LED 12W | Screw In - Light Emitting Diode Lamp, (1) 12W | Electronic |  | 1 | 12 | 12 | SLED12/1 | Screw-In
SLED13/1 | LED | LED Screw-In | LED 13W | Screw In - Light Emitting Diode Lamp, (1) 13W | Electronic |  | 1 | 13 | 13 | SLED13/1 | Screw-In
SLED14/1 | LED | LED Screw-In | LED 14W | Screw In - Light Emitting Diode Lamp, (1) 14W | Electronic |  | 1 | 14 | 14 | SLED14/1 | Screw-In
SLED15/1 | LED | LED Screw-In | LED 15W | Screw In - Light Emitting Diode Lamp, (1) 15W | Electronic |  | 1 | 15 | 15 | SLED15/1 | Screw-In
SLED16/1 | LED | LED Screw-In | LED 16W | Screw In - Light Emitting Diode Lamp, (1) 16W | Electronic |  | 1 | 16 | 16 | SLED16/1 | Screw-In
SLED17/1 | LED | LED Screw-In | LED 17W | Screw In - Light Emitting Diode Lamp, (1) 17W | Electronic |  | 1 | 17 | 17 | SLED17/1 | Screw-In
SLED18/1 | LED | LED Screw-In | LED 18W | Screw In - Light Emitting Diode Lamp, (1) 18W | Electronic |  | 1 | 18 | 18 | SLED18/1 | Screw-In
SLED19/1 | LED | LED Screw-In | LED 19W | Screw In - Light Emitting Diode Lamp, (1) 19W | Electronic |  | 1 | 19 | 19 | SLED19/1 | Screw-In
SLED20/1 | LED | LED Screw-In | LED 20W | Screw In - Light Emitting Diode Lamp, (1) 20W | Electronic |  | 1 | 20 | 20 | SLED20/1 | Screw-In
SLED21/1 | LED | LED Screw-In | LED 21W | Screw In - Light Emitting Diode Lamp, (1) 21W | Electronic |  | 1 | 21 | 21 | SLED21/1 | Screw-In
SLED22/1 | LED | LED Screw-In | LED 22W | Screw In - Light Emitting Diode Lamp, (1) 22W | Electronic |  | 1 | 22 | 22 | SLED22/1 | Screw-In
SLED26/1 | LED | LED Screw-In | LED 26W | Screw In - Light Emitting Diode Lamp, (1) 26W | Electronic |  | 1 | 26 | 26 | SLED26/1 | Screw-In
CF10/2D | CFL | CFL Fixture | CFD10W | Compact Fluorescent, 2D, (1) 10W lamp | Mag-STD |  | 1 | 10 | 16 | CF10/2D | General
CF10/2D-L | CFL | CFL Fixture | CFD10W | Compact Fluorescent, 2D, (1) 10W lamp | Electronic |  | 1 | 10 | 12 | CF10/2D-L | General
CF11/1 | CFL | CFL Fixture | CF11W | Compact Fluorescent, (1) 11W lamp | Mag-STD |  | 1 | 11 | 13 | CF11/1 | General
CF16/2D | CFL | CFL Fixture | CFD16W | Compact Fluorescent, 2D, (1) 16W lamp | Mag-STD |  | 1 | 16 | 26 | CF16/2D | General
CF16/2D-L | CFL | CFL Fixture | CFD16W | Compact Fluorescent, 2D, (1) 16W lamp | Electronic |  | 1 | 16 | 18 | CF16/2D-L | General
CF21/2D | CFL | CFL Fixture | CFD21W | Compact Fluorescent, 2D, (1) 21W lamp | Mag-STD |  | 1 | 21 | 26 | CF21/2D | General
CF21/2D-L | CFL | CFL Fixture | CFD21W | Compact Fluorescent, 2D, (1) 21W lamp | Electronic |  | 1 | 21 | 22 | CF21/2D-L | General
CF23/1 | CFL | CFL Fixture | CF23W | Compact Fluorescent, (1) 23W lamp | Mag-STD |  | 1 | 23 | 29 | CF23/1 | General
CF23/1-L | CFL | CFL Fixture | CF23W | Compact Fluorescent, (1) 23W lamp | Electronic |  | 1 | 23 | 25 | CF23/1-L | General
CF28/2D | CFL | CFL Fixture | CFD28W | Compact Fluorescent, 2D, (1) 28W lamp | Mag-STD |  | 1 | 28 | 35 | CF28/2D | General
CF28/2D-L | CFL | CFL Fixture | CFD28W | Compact Fluorescent, 2D, (1) 28W lamp | Electronic |  | 1 | 28 | 28 | CF28/2D-L | General
CF38/2D | CFL | CFL Fixture | CFD38W | Compact Fluorescent, 2D, (1) 38W lamp | Mag-STD |  | 1 | 38 | 46 | CF38/2D | General
CF38/2D-L | CFL | CFL Fixture | CFD38W | Compact Fluorescent, 2D, (1) 38W lamp | Electronic |  | 1 | 38 | 36 | CF38/2D-L | General
CF42/1-L | CFL | CFL Fixture | CF42W | Compact Fluorescent, (1) 42W lamp | Electronic |  | 1 | 42 | 48 | CF42/1-L | General
CFQ10/1 | CFL | CFL Fixture | CFQ10W | Compact Fluorescent, quad, (1) 10W lamp | Mag-STD |  | 1 | 10 | 15 | CFQ10/1 | General
CFQ13/1 | CFL | CFL Fixture | CFQ13W | Compact Fluorescent, quad, (1) 13W lamp | Mag-STD |  | 1 | 13 | 17 | CFQ13/1 | General
CFQ13/1-L | CFL | CFL Fixture | CFQ13W | Compact Fluorescent, quad, (1) 13W lamp, BF=1.05 | Electronic |  | 1 | 13 | 15 | CFQ13/1-L | General
CFQ15/1 | CFL | CFL Fixture | CFQ15W | Compact Fluorescent, quad, (1) 15W lamp | Mag-STD |  | 1 | 15 | 20 | CFQ15/1 | General
CFQ17/1 | CFL | CFL Fixture | CFQ17W | Compact Fluorescent, quad, (1) 17W lamp | Mag-STD |  | 1 | 17 | 24 | CFQ17/1 | General
CFQ18/1 | CFL | CFL Fixture | CFQ18W | Compact Fluorescent, quad, (1) 18W lamp | Mag-STD |  | 1 | 18 | 26 | CFQ18/1 | General
CFQ18/1-L | CFL | CFL Fixture | CFQ18W | Compact Fluorescent, quad, (1) 18W lamp, BF=1.0 | Electronic |  | 1 | 18 | 20 | CFQ18/1-L | General
CFQ20/1 | CFL | CFL Fixture | CFQ20W | Compact Fluorescent, quad, (1) 20W lamp | Mag-STD |  | 1 | 20 | 23 | CFQ20/1 | General
CFQ22/1 | CFL | CFL Fixture | CFQ22W | Compact Fluorescent, quad, (1) 22W lamp | Mag-STD |  | 1 | 22 | 24 | CFQ22/1 | General
CFQ25/1 | CFL | CFL Fixture | CFQ25W | Compact Fluorescent, quad, (1) 25W lamp | Mag-STD |  | 1 | 25 | 33 | CFQ25/1 | General
CFQ26/1 | CFL | CFL Fixture | CFQ26W | Compact Fluorescent, quad, (1) 26W lamp | Mag-STD |  | 1 | 26 | 33 | CFQ26/1 | General
CFQ26/1-L | CFL | CFL Fixture | CFQ26W | Compact Fluorescent, quad, (1) 26W lamp, BF=0.95 | Electronic |  | 1 | 26 | 27 | CFQ26/1-L | General
CFQ28/1 | CFL | CFL Fixture | CFQ28W | Compact Fluorescent, quad, (1) 28W lamp | Mag-STD |  | 1 | 28 | 33 | CFQ28/1 | General
CFQ9/1 | CFL | CFL Fixture | CFQ9W | Compact Fluorescent, quad, (1) 9W lamp | Mag-STD |  | 1 | 9 | 14 | CFQ9/1 | General
CFS7/1 | CFL | CFL Fixture | CFS7W | Compact Fluorescent, spiral, (1) 7W lamp | Electronic |  | 1 | 7 | 7 | CFS7/1 | General
CFS9/1 | CFL | CFL Fixture | CFS9W | Compact Fluorescent, spiral, (1) 9W lamp | Electronic |  | 1 | 9 | 9 | CFS9/1 | General
CFS11/1 | CFL | CFL Fixture | CFS11W | Compact Fluorescent, spiral, (1) 11W lamp | Electronic |  | 1 | 11 | 11 | CFS11/1 | General
CFS13/1 | CFL | CFL Fixture | CFS13W | Compact Fluorescent, spiral, (1) 13W lamp | Electronic |  | 1 | 13 | 13 | CFS13/1 | General
CFS15/1 | CFL | CFL Fixture | CFS15W | Compact Fluorescent, spiral, (1) 15W lamp | Electronic |  | 1 | 15 | 15 | CFS15/1 | General
CFS20/1 | CFL | CFL Fixture | CFS20W | Compact Fluorescent, spiral, (1) 20W lamp | Electronic |  | 1 | 20 | 20 | CFS20/1 | General
CFS23/1 | CFL | CFL Fixture | CFS23W | Compact Fluorescent, spiral, (1) 23W lamp | Electronic |  | 1 | 23 | 23 | CFS23/1 | General
CFS26/1 | CFL | CFL Fixture | CFS26W | Compact Fluorescent, spiral, (1) 26W lamp | Electronic |  | 1 | 26 | 26 | CFS26/1 | General
CFS27/1 | CFL | CFL Fixture | CFS27W | Compact Fluorescent, spiral, (1) 27W lamp | Electronic |  | 1 | 27 | 27 | CFS27/1 | General
CFT13/1 | CFL | CFL Fixture | CFT13W | Compact Fluorescent, twin, (1) 13W lamp | Mag-STD |  | 1 | 13 | 17 | CFT13/1 | General
CFT18/1 | CFL | CFL Fixture | CFT18W | Compact Fluorescent, long twin., (1) 18W lamp | Mag-STD |  | 1 | 18 | 24 | CFT18/1 | General
CFT22/1 | CFL | CFL Fixture | CFT22W | Compact Fluorescent, twin, (1) 22W lamp | Mag-STD |  | 1 | 22 | 27 | CFT22/1 | General
CFT24/1 | CFL | CFL Fixture | CFT24W | Compact Fluorescent, long twin, (1) 24W lamp | Mag-STD |  | 1 | 24 | 32 | CFT24/1 | General
CFT28/1 | CFL | CFL Fixture | CFT28W | Compact Fluorescent, twin, (1) 28W lamp | Mag-STD |  | 1 | 28 | 33 | CFT28/1 | General
CFT32/1-L | CFL | CFL Fixture | CFM32W | Compact Fluorescent, twin or multi, (1) 32W lamp | Electronic |  | 1 | 32 | 34 | CFT32/1-L | General
CFT36/1 | CFL | CFL Fixture | CFT36W | Compact Fluorescent, long twin, (1) 36W lamp | Mag-STD |  | 1 | 36 | 51 | CFT36/1 | General
CFT40/1 | CFL | CFL Fixture | CFT40W | Compact Fluorescent, twin, (1) 40W lamp | Mag-STD |  | 1 | 40 | 46 | CFT40/1 | General
CFT40/1-BX | CFL | CFL Fixture | CFT40W | Compact Fluorescent, Biax, (1) 40W lamp | Electronic |  | 1 | 40 | 46 | CFT40/1-BX | General
CFT40/1-L | CFL | CFL Fixture | CFT40W | Compact Fluorescent, long twin, (1) 40W lamp | Electronic |  | 1 | 40 | 43 | CFT40/1-L | General
CFT05/1 | CFL | CFL Fixture | CFT5W | Compact Fluorescent, twin, (1) 5W lamp | Mag-STD |  | 1 | 5 | 9 | CFT5/1 | General
CFT50/1-BX | CFL | CFL Fixture | CFT50W | Compact Fluorescent, Biax, (1) 50W lamp | Electronic |  | 1 | 50 | 54 | CFT50/1-BX | General
CFT55/1-BX | CFL | CFL Fixture | CFT55W | Compact Fluorescent, Biax, (1) 55W lamp | Electronic |  | 1 | 55 | 56 | CFT55/1-BX | General
CFT7/1 | CFL | CFL Fixture | CFT7W | Compact Fluorescent, twin, (1) 7W lamp | Mag-STD |  | 1 | 7 | 10 | CFT7/1 | General
CFT9/1 | CFL | CFL Fixture | CFT9W | Compact Fluorescent, twin, (1) 9W lamp | Mag-STD |  | 1 | 9 | 11 | CFT9/1 | General
CF11/2 | CFL | CFL Fixture | CF11W | Compact Fluorescent, (2) 11W lamp | Mag-STD |  | 2 | 11 | 26 | CF11/2 | General
CF42/2-L | CFL | CFL Fixture | CF42W | Compact Fluorescent, (2) 42W lamp | Electronic |  | 2 | 42 | 100 | CF42/2-L | General
CFQ13/2 | CFL | CFL Fixture | CFQ13W | Compact Fluorescent, quad, (2) 13W lamp | Mag-STD |  | 2 | 13 | 31 | CFQ13/2 | General
CFQ13/2-L | CFL | CFL Fixture | CFQ13W | Compact Fluorescent, quad, (2) 13W lamp, BF=1.0 | Electronic |  | 2 | 13 | 28 | CFQ13/2-L | General
CFQ17/2 | CFL | CFL Fixture | CFQ17W | Compact Fluorescent, quad, (2) 17W lamp | Mag-STD |  | 2 | 17 | 48 | CFQ17/2 | General
CFQ18/2 | CFL | CFL Fixture | CFQ18W | Compact Fluorescent, quad, (2) 18W lamp | Mag-STD |  | 2 | 18 | 45 | CFQ18/2 | General
CFQ18/2-L | CFL | CFL Fixture | CFQ18W | Compact Fluorescent, quad, (2) 18W lamp, BF=1.0 | Electronic |  | 2 | 18 | 38 | CFQ18/2-L | General
CFQ20/2 | CFL | CFL Fixture | CFQ20W | Compact Fluorescent, quad, (2) 20W lamp | Mag-STD |  | 2 | 20 | 46 | CFQ20/2 | General
CFQ22/2 | CFL | CFL Fixture | CFQ22W | Compact Fluorescent, quad, (2) 22W lamp | Mag-STD |  | 2 | 22 | 48 | CFQ22/2 | General
CFQ25/2 | CFL | CFL Fixture | CFQ25W | Compact Fluorescent, quad, (2) 25W lamp | Mag-STD |  | 2 | 25 | 66 | CFQ25/2 | General
CFQ26/2 | CFL | CFL Fixture | CFQ26W | Compact Fluorescent, quad, (2) 26W lamp | Mag-STD |  | 2 | 26 | 66 | CFQ26/2 | General
CFQ26/2-L | CFL | CFL Fixture | CFQ26W | Compact Fluorescent, quad, (2) 26W lamp, BF=0.95 | Electronic |  | 2 | 26 | 50 | CFQ26/2-L | General
CFQ9/2 | CFL | CFL Fixture | CFQ9W | Compact Fluorescent, quad, (2) 9W lamp | Mag-STD |  | 2 | 9 | 23 | CFQ9/2 | General
CFT13/2 | CFL | CFL Fixture | CFT13W | Compact Fluorescent, twin, (2) 13W lamp | Mag-STD |  | 2 | 13 | 31 | CFT13/2 | General
CFT22/2 | CFL | CFL Fixture | CFT22W | Compact Fluorescent, twin, (2) 22W lamp | Mag-STD |  | 2 | 22 | 54 | CFT22/2 | General
CFT28/2 | CFL | CFL Fixture | CFT28W | Compact Fluorescent, twin, (2) 28W lamp | Mag-STD |  | 2 | 28 | 66 | CFT28/2 | General
CFT32/2-L | CFL | CFL Fixture | CFM32W | Compact Fluorescent, twin or multi, (2) 32W lamp | Electronic |  | 2 | 32 | 62 | CFT32/2-L | General
CFT40/2 | CFL | CFL Fixture | CFT40W | Compact Fluorescent, twin, (2) 40W lamp | Mag-STD |  | 2 | 40 | 85 | CFT40/2 | General
CFT40/2-BX | CFL | CFL Fixture | CFT40W | Compact Fluorescent, Biax, (2) 40W lamp | Electronic |  | 2 | 40 | 72 | CFT40/2-BX | General
CFT40/2-L | CFL | CFL Fixture | CFT40W | Compact Fluorescent, long twin, (2) 40W lamp | Electronic |  | 2 | 40 | 72 | CFT40/2-L | General
CFT5/2 | CFL | CFL Fixture | CFT5W | Compact Fluorescent, twin, (2) 5W lamp | Mag-STD |  | 2 | 5 | 18 | CFT5/2 | General
CFT50/2-BX | CFL | CFL Fixture | CFT50W | Compact Fluorescent, Biax, (2) 50W lamp | Electronic |  | 2 | 50 | 108 | CFT50/2-BX | General
CFT55/2-BX | CFL | CFL Fixture | CFT55W | Compact Fluorescent, Biax, (2) 55W lamp | Electronic |  | 2 | 55 | 112 | CFT55/2-BX | General
CFT7/2 | CFL | CFL Fixture | CFT7W | Compact Fluorescent, twin, (2) 7W lamp | Mag-STD |  | 2 | 7 | 21 | CFT7/2 | General
CFT9/2 | CFL | CFL Fixture | CFT9W | Compact Fluorescent, twin, (2) 9W lamp | Mag-STD |  | 2 | 9 | 23 | CFT9/2 | General
CF18/3-L | CFL | CFL Fixture | CF18W | Compact Fluorescent, (3) 18W lamp | Electronic |  | 3 | 18 | 60 | CF18/3-L | General
CF26/3-L | CFL | CFL Fixture | CF26W | Compact Fluorescent, (3) 26W lamp | Electronic |  | 3 | 26 | 82 | CF26/3-L | General
CF32/3-L | CFL | CFL Fixture | CF32W | Compact Fluorescent, (3) 32W lamp | Electronic |  | 3 | 32 | 114 | CF32/3-L | General
CF42/3-L | CFL | CFL Fixture | CF42W | Compact Fluorescent, (3) 42W lamp | Electronic |  | 3 | 42 | 141 | CF42/3-L | General
CFQ13/3 | CFL | CFL Fixture | CFQ13W | Compact Fluorescent, quad, (3) 13W lamp | Mag-STD |  | 3 | 13 | 48 | CFQ13/3 | General
CFQ22/3 | CFL | CFL Fixture | CFQ22W | Compact Fluorescent, quad, (3) 22W lamp | Mag-STD |  | 3 | 22 | 72 | CFQ22/3 | General
CFQ26/3 | CFL | CFL Fixture | CFQ26W | Compact Fluorescent, quad, (3) 26W lamp | Mag-STD |  | 3 | 26 | 99 | CFQ26/3 | General
CFT13/3 | CFL | CFL Fixture | CFT13W | Compact Fluorescent, twin, (3) 13 W lamp | Mag-STD |  | 3 | 13 | 48 | CFT13/3 | General
CFT40/3 | CFL | CFL Fixture | CFT40W | Compact Fluorescent, twin, (3) 40 W lamp | Mag-STD |  | 3 | 40 | 133 | CFT40/3 | General
CFT40/3-BX | CFL | CFL Fixture | CFT40W | Compact Fluorescent, Biax, (3) 40W lamp | Electronic |  | 3 | 40 | 102 | CFT40/3-BX | General
CFT40/3-L | CFL | CFL Fixture | CFT40W | Compact Fluorescent, long twin, (3) 40W lamp | Electronic |  | 3 | 40 | 105 | CFT40/3-L | General
CFT50/3-BX | CFL | CFL Fixture | CFT50W | Compact Fluorescent, Biax, (3) 50W lamp | Electronic |  | 3 | 50 | 162 | CFT50/3-BX | General
CFT55/3-BX | CFL | CFL Fixture | CFT55W | Compact Fluorescent, Biax, (3) 55W lamp | Electronic |  | 3 | 55 | 168 | CFT55/3-BX | General
CFT9/3 | CFL | CFL Fixture | CFT9W | Compact Fluorescent, twin, (3) 9W lamp | Mag-STD |  | 3 | 9 | 34 | CFT9/3 | General
CF26/4-L | CFL | CFL Fixture | CF26W | Compact Fluorescent, (4) 26W lamp | Electronic |  | 4 | 26 | 108 | CF26/4-L | General
CF32/4-L | CFL | CFL Fixture | CF32W | Compact Fluorescent, (4) 32W lamp | Electronic |  | 4 | 32 | 152 | CF32/4-L | General
CF42/4-L | CFL | CFL Fixture | CF42W | Compact Fluorescent, (4) 42W lamp | Electronic |  | 4 | 42 | 188 | CF42/4-L | General
CFQ18/4 | CFL | CFL Fixture | CFQ18W | Compact Fluorescent, quad, (4) 18W lamp | Mag-STD |  | 4 | 18 | 90 | CFQ18/4 | General
CFT22/4 | CFL | CFL Fixture | CFT22W | Compact Fluorescent, twin, (4) 22W lamp | Mag-STD |  | 4 | 22 | 108 | CFT22/4 | General
CFT36/4-BX | CFL | CFL Fixture | CFT36W | Compact Fluorescent, Biax, (4) 36W lamp | Electronic |  | 4 | 36 | 148 | CFT36/4-BX | General
CFT40/4-BX | CFL | CFL Fixture | CFT40W | Compact Fluorescent, Biax, (4) 40W lamp | Electronic |  | 4 | 40 | 144 | CFT40/4-BX | General
CFT50/4-BX | CFL | CFL Fixture | CFT50W | Compact Fluorescent, Biax, (4) 50W lamp | Electronic |  | 4 | 50 | 216 | CFT50/4-BX | General
CFT55/4-BX | CFL | CFL Fixture | CFT55W | Compact Fluorescent, Biax, (4) 55W lamp | Electronic |  | 4 | 55 | 224 | CFT55/4-BX | General
CFT40/5-BX | CFL | CFL Fixture | CFT40W | Compact Fluorescent, Biax, (5) 40W lamp | Electronic |  | 5 | 40 | 190 | CFT40/5-BX | General
CFT50/5-BX | CFL | CFL Fixture | CFT50W | Compact Fluorescent, Biax, (5) 50W lamp | Electronic |  | 5 | 50 | 270 | CFT50/5-BX | General
CFT55/5-BX | CFL | CFL Fixture | CFT55W | Compact Fluorescent, Biax, (5) 55W lamp | Electronic |  | 5 | 55 | 280 | CFT55/5-BX | General
CF26/6-L | CFL | CFL Fixture | CF26W | Compact Fluorescent, (6) 26W lamp | Electronic |  | 6 | 26 | 162 | CF26/6-L | General
CF32/6-L | CFL | CFL Fixture | CF32W | Compact Fluorescent, (6) 32W lamp | Electronic |  | 6 | 32 | 228 | CF32/6-L | General
CF42/6-L | CFL | CFL Fixture | CF42W | Compact Fluorescent, (6) 42W lamp | Electronic |  | 6 | 42 | 282 | CF42/6-L | General
CFQ26/6-L | CFL | CFL Fixture | CFQ26W | Compact Fluorescent, quad, (6) 26W lamp, BF=0.95 | Electronic |  | 6 | 26 | 150 | CFQ26/6-L | General
CFT32/6-L | CFL | CFL Fixture | CFM32W | Compact Fluorescent, twin or multi, (6) 32W lamp | Electronic |  | 6 | 32 | 186 | CFT32/6-L | General
CFT36/6-BX | CFL | CFL Fixture | CFT36W | Compact Fluorescent, Biax, (6) 36W lamp | Electronic |  | 6 | 36 | 212 | CFT36/6-BX | General
CFT36/6-L | CFL | CFL Fixture | CFT36W | Compact Fluorescent, long Twin, (6) 36W lamp | Electronic |  | 6 | 36 | 198 | CFT36/6-L | General
CFT36/6-LH | CFL | CFL Fixture | CFT36W | Compact Fluorescent, long Twin, (6) 36W lamp/ High Ballast Factor | Electronic |  | 6 | 36 | 210 | CFT36/6-LH | General
CFT40/6-BX | CFL | CFL Fixture | CFT40W | Compact Fluorescent, Biax, (6) 40W lamp | Electronic |  | 6 | 40 | 204 | CFT40/6-BX | General
CFT40/6-L | CFL | CFL Fixture | CFT40W | Compact Fluorescent, long Twin, (6) 40W lamp | Electronic |  | 6 | 40 | 220 | CFT40/6-L | General
CFT40/6-LH | CFL | CFL Fixture | CFT40W | Compact Fluorescent, long Twin, (6) 40W lamp/ High Ballast Factor | Electronic |  | 6 | 40 | 233 | CFT40/6-LH | General
CFT50/6-BX | CFL | CFL Fixture | CFT50W | Compact Fluorescent, Biax, (6) 50W lamp | Electronic |  | 6 | 50 | 324 | CFT50/6-BX | General
CFT55/6-BX | CFL | CFL Fixture | CFT55W | Compact Fluorescent, Biax, (6) 55W lamp | Electronic |  | 6 | 55 | 336 | CFT55/6-BX | General
CFT55/6-L | CFL | CFL Fixture | CFT55W | Compact Fluorescent, long Twin, (6) 55W lamp | Electronic |  | 6 | 55 | 352 | CFT55/6-L | General
CFT55/6-LH | CFL | CFL Fixture | CFT55W | Compact Fluorescent, long Twin, (6) 55W lamp/ High Ballast Factor | Electronic |  | 6 | 55 | 373 | CFT55/6-LH | General
CF26/8-L | CFL | CFL Fixture | CF26W | Compact Fluorescent, (8) 26W lamp | Electronic |  | 8 | 26 | 216 | CF26/8-L | General
CF32/8-L | CFL | CFL Fixture | CF32W | Compact Fluorescent, (8) 32W lamp | Electronic |  | 8 | 32 | 304 | CF32/8-L | General
CF42/8-L | CFL | CFL Fixture | CF42W | Compact Fluorescent, (8) 42W lamp | Electronic |  | 8 | 42 | 376 | CF42/8-L | General
CFT36/8-BX | CFL | CFL Fixture | CFT36W | Compact Fluorescent, Biax, (8) 36W lamp | Electronic |  | 8 | 36 | 296 | CFT36/8-BX | General
CFT36/8-L | CFL | CFL Fixture | CFT36W | Compact Fluorescent, long Twin, (8) 36W lamp | Electronic |  | 8 | 36 | 270 | CFT36/8-L | General
CFT36/8-LH | CFL | CFL Fixture | CFT36W | Compact Fluorescent, long Twin, (8) 36W lamp/ High Ballast Factor | Electronic |  | 8 | 36 | 286 | CFT36/8-LH | General
CFT40/8-BX | CFL | CFL Fixture | CFT40W | Compact Fluorescent, Biax, (8) 40W lamp | Electronic |  | 8 | 40 | 288 | CFT40/8-BX | General
CFT40/8-L | CFL | CFL Fixture | CFT40W | Compact Fluorescent, long Twin, (8) 40W lamp | Electronic |  | 8 | 40 | 300 | CFT40/8-L | General
CFT40/8-LH | CFL | CFL Fixture | CFT40W | Compact Fluorescent, long Twin, (8) 40W lamp/ High Ballast Factor | Electronic |  | 8 | 40 | 340 | CFT40/8-LH | General
CFT50/8-BX | CFL | CFL Fixture | CFT50W | Compact Fluorescent, Biax, (8) 50W lamp | Electronic |  | 8 | 50 | 432 | CFT50/8-BX | General
CFT55/8-BX | CFL | CFL Fixture | CFT55W | Compact Fluorescent, Biax, (8) 55W lamp | Electronic |  | 8 | 55 | 448 | CFT55/8-BX | General
CFT55/8-L | CFL | CFL Fixture | CFT55W | Compact Fluorescent, long Twin, (8) 55W lamp | Electronic |  | 8 | 55 | 468 | CFT55/8-L | General
CFT55/8-LH | CFL | CFL Fixture | CFT55W | Compact Fluorescent, long Twin, (8) 55W lamp/ High Ballast Factor | Electronic |  | 8 | 55 | 496 | CFT55/8-LH | General
CFT36/9-BX | CFL | CFL Fixture | CFT36W | Compact Fluorescent, Biax, (9) 36W lamp | Electronic |  | 9 | 36 | 318 | CFT36/9-BX | General
CFT40/9-BX | CFL | CFL Fixture | CFT40W | Compact Fluorescent, Biax, (9) 40W lamp | Electronic |  | 9 | 40 | 306 | CFT40/9-BX | General
CFT50/9-BX | CFL | CFL Fixture | CFT50W | Compact Fluorescent, Biax, (9) 50W lamp | Electronic |  | 9 | 50 | 486 | CFT50/9-BX | General
CFT55/9-BX | CFL | CFL Fixture | CFT55W | Compact Fluorescent, Biax, (9) 55W lamp | Electronic |  | 9 | 55 | 504 | CFT55/9-BX | General
CFT40/12-BX | CFL | CFL Fixture | CFT40W | Compact Fluorescent, Biax, (12) 40W lamp | Electronic |  | 12 | 40 | 408 | CFT40/12-BX | General
CFT50/12-BX | CFL | CFL Fixture | CFT50W | Compact Fluorescent, Biax, (12) 50W lamp | Electronic |  | 12 | 50 | 648 | CFT50/12-BX | General
CFT55/12-BX | CFL | CFL Fixture | CFT55W | Compact Fluorescent, Biax, (12) 55W lamp | Electronic |  | 12 | 55 | 672 | CFT55/12-BX | General
CFC7/1 | CFL | CFL Screw-In | CFC7 | Compact Fluorescent, Screw-in, (1) 7W lamp | Electronic |  | 1 | 7 | 7 | CFC7/1 | Screw-In
CFC9/1 | CFL | CFL Screw-In | CFC9 | Compact Fluorescent, Screw-in, (1) 9W lamp | Electronic |  | 1 | 9 | 9 | CFC9/1 | Screw-In
CFC11/1 | CFL | CFL Screw-In | CFC11 | Compact Fluorescent, Screw-in, (1) 11W lamp | Electronic |  | 1 | 11 | 11 | CFC11/1 | Screw-In
CFC12/1 | CFL | CFL Screw-In | CFC12 | Compact Fluorescent, Screw-in, (1) 12W lamp | Electronic |  | 1 | 12 | 12 | CFC12/1 | Screw-In
CFC13/1 | CFL | CFL Screw-In | CFC13 | Compact Fluorescent, Screw-in, (1) 13W lamp | Electronic |  | 1 | 13 | 13 | CFC13/1 | Screw-In
CFC14/1 | CFL | CFL Screw-In | CFC14 | Compact Fluorescent, Screw-in, (1) 14W lamp | Electronic |  | 1 | 14 | 14 | CFC14/1 | Screw-In
CFC15/1 | CFL | CFL Screw-In | CFC15 | Compact Fluorescent, Screw-in, (1) 15W lamp | Electronic |  | 1 | 15 | 15 | CFC15/1 | Screw-In
CFC16/1 | CFL | CFL Screw-In | CFC16 | Compact Fluorescent, Screw-in, (1) 16W lamp | Electronic |  | 1 | 16 | 16 | CFC16/1 | Screw-In
CFC17/1 | CFL | CFL Screw-In | CFC17 | Compact Fluorescent, Screw-in, (1) 17W lamp | Electronic |  | 1 | 17 | 17 | CFC17/1 | Screw-In
CFC18/1 | CFL | CFL Screw-In | CFC18 | Compact Fluorescent, Screw-in, (1) 18W lamp | Electronic |  | 1 | 18 | 18 | CFC18/1 | Screw-In
CFC20/1 | CFL | CFL Screw-In | CFC20 | Compact Fluorescent, Screw-in, (1) 20W lamp | Electronic |  | 1 | 20 | 20 | CFC20/1 | Screw-In
CFC23/1 | CFL | CFL Screw-In | CFC23 | Compact Fluorescent, Screw-in, (1) 23W lamp | Electronic |  | 1 | 23 | 23 | CFC23/1 | Screw-In
CFC26/1 | CFL | CFL Screw-In | CFC26 | Compact Fluorescent, Screw-in, (1) 26W lamp | Electronic |  | 1 | 26 | 26 | CFC26/1 | Screw-In
CFC30/1 | CFL | CFL Screw-In | CFC30 | Compact Fluorescent, Screw-in, (1) 30W lamp | Electronic |  | 1 | 30 | 30 | CFC30/1 | Screw-In
CCFC1.5/1 | CFL | Cold Cathode CFL | CCFC1.5 | Cold-Cathode Compact Fluorescent, Screw-in, (1) 1.5W lamp | Electronic |  | 1 | 1.5 | 1.5 | CCFC1.5/1 | Screw-In
CCFC3/1 | CFL | Cold Cathode CFL | CCFC3 | Cold-Cathode Compact Fluorescent, Screw-in, (1) 3W lamp | Electronic |  | 1 | 3 | 3 | CCFC3/1 | Screw-In
CCFC5/1 | CFL | Cold Cathode CFL | CCFC5 | Cold-Cathode Compact Fluorescent, Screw-in, (1) 5W lamp | Electronic |  | 1 | 5 | 5 | CCFC5/1 | Screw-In
CCFC8/1 | CFL | Cold Cathode CFL | CCFC8 | Cold-Cathode Compact Fluorescent, Screw-in, (1) 8W lamp | Electronic |  | 1 | 8 | 8 | CCFC8/1 | Screw-In
F1.51LS | Linear Fluorescent | T8 Linear Fluorescent | F15T8 | Fluorescent, (1) 18" T8 lamp | Mag-STD | 12 | 1 | 15 | 19 | F1.51LS | General
F1.52LS | Linear Fluorescent | T8 Linear Fluorescent | F15T8 | Fluorescent, (2) 18" T8 lamp | Mag-STD | 12 | 2 | 15 | 36 | F1.52LS | General
F21ILL | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 24 | 1 | 17 | 20 | F21ILL | General
F21ILL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 24 | 1 | 17 | 17 | F21ILL/T2 | General
F21ILL/T2-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 2 Lamp Ballast | Electronic | 24 | 1 | 17 | 15 | F21ILL/T2-R | General
F21ILL/T3 | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 24 | 1 | 17 | 16 | F21ILL/T3 | General
F21ILL/T3-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 3 Lamp Ballast | Electronic | 24 | 1 | 17 | 14 | F21ILL/T3-R | General
F21ILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 24 | 1 | 17 | 15 | F21ILL/T4 | General
F21ILL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 4 Lamp Ballast | Electronic | 24 | 1 | 17 | 14 | F21ILL/T4-R | General
F21LL | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 24 | 1 | 17 | 16 | F21LL | General
F21LL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 24 | 1 | 17 | 16 | F21LL/T2 | General
F21LL/T3 | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 24 | 1 | 17 | 17 | F21LL/T3 | General
F21LL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 24 | 1 | 17 | 17 | F21LL/T4 | General
F21LL-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 24 | 1 | 17 | 15 | F21LL-R | General
F21LS | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T8 lamp, Standard Ballast | Mag-STD | 24 | 1 | 17 | 24 | F21LS | General
F22ILE | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (2) 24", T-8 Instant Start lamp, Energy Saving Magnetic Ballast | Mag-ES | 24 | 2 | 17 | 45 | F22ILE | General
F22ILL | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (2) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 24 | 2 | 17 | 33 | F22ILL | General
F22ILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (2) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 24 | 2 | 17 | 31 | F22ILL/T4 | General
F22ILL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (2) 24", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 4 Lamp Ballast | Electronic | 24 | 2 | 17 | 28 | F22ILL/T4-R | General
F22ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (2) 24", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 24 | 2 | 17 | 29 | F22ILL-R | General
F22LL | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (2) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 24 | 2 | 17 | 31 | F22LL | General
F22LL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (2) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 24 | 2 | 17 | 34 | F22LL/T4 | General
F22LL-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (2) 24", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 24 | 2 | 17 | 28 | F22LL-R | General
F23ILL | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (3) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 24 | 3 | 17 | 47 | F23ILL | General
F23ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (3) 24", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 24 | 3 | 17 | 49 | F23ILL-H | General
F23ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (3) 24", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 24 | 3 | 17 | 43 | F23ILL-R | General
F23LL | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (3) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 24 | 3 | 17 | 52 | F23LL | General
F23LL-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (3) 24", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 24 | 3 | 17 | 41 | F23LL-R | General
F24ILL | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (4) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 24 | 4 | 17 | 61 | F24ILL | General
F24ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (4) 24", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 24 | 4 | 17 | 55 | F24ILL-R | General
F24LL | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (4) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 24 | 4 | 17 | 68 | F24LL | General
F24LL-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (4) 24", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 24 | 4 | 17 | 57 | F24LL-R | General
F31ILL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 36 | 1 | 25 | 26 | F31ILL | General
F31ILL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 36 | 1 | 25 | 23 | F31ILL/T2 | General
F31ILL/T2-H | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, HLO (BF: .96-1.1), Tandem 2 Lamp Ballast | Electronic | 36 | 1 | 25 | 24 | F31ILL/T2-H | General
F31ILL/T2-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, RLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 36 | 1 | 25 | 23 | F31ILL/T2-R | General
F31ILL/T3 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 36 | 1 | 25 | 22 | F31ILL/T3 | General
F31ILL/T3-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 3 Lamp Ballast | Electronic | 36 | 1 | 25 | 22 | F31ILL/T3-R | General
F31ILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 36 | 1 | 25 | 22 | F31ILL/T4 | General
F31ILL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 4 Lamp Ballast | Electronic | 36 | 1 | 25 | 22 | F31ILL/T4-R | General
F31ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 36 | 1 | 25 | 28 | F31ILL-H | General
F31ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 36 | 1 | 25 | 27 | F31ILL-R | General
F31LL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 36 | 1 | 25 | 24 | F31LL | General
F31LL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 36 | 1 | 25 | 23 | F31LL/T2 | General
F31LL/T3 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 36 | 1 | 25 | 24 | F31LL/T3 | General
F31LL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 36 | 1 | 25 | 22 | F31LL/T4 | General
F31LL-H | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1) | Electronic | 36 | 1 | 25 | 26 | F31LL-H | General
F31LL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 36 | 1 | 25 | 23 | F31LL-R | General
F32ILL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 36 | 2 | 25 | 46 | F32ILL | General
F32ILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 36 | 2 | 25 | 44 | F32ILL/T4 | General
F32ILL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 4 Lamp Ballast | Electronic | 36 | 2 | 25 | 43 | F32ILL/T4-R | General
F32ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 36 | 2 | 25 | 48 | F32ILL-H | General
F32ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 36 | 2 | 25 | 46 | F32ILL-R | General
F32LE | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp | Mag-ES | 36 | 2 | 25 | 65 | F32LE | General
F32LL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 36 | 2 | 25 | 46 | F32LL | General
F32LL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 36 | 2 | 25 | 45 | F32LL/T4 | General
F32LL-H | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1) | Electronic | 36 | 2 | 25 | 50 | F32LL-H | General
F32LL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 36 | 2 | 25 | 42 | F32LL-R | General
F32LL-V | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp, Rapid Start Ballast, VHLO (BF>1.1) | Electronic | 36 | 2 | 25 | 70 | F32LL-V | General
F33ILL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (3) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 36 | 3 | 25 | 67 | F33ILL | General
F33ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (3) 36", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 36 | 3 | 25 | 66 | F33ILL-R | General
F33LL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (3) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 36 | 3 | 25 | 72 | F33LL | General
F33LL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (3) 36", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 36 | 3 | 25 | 62 | F33LL-R | General
F34ILL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (4) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 36 | 4 | 25 | 87 | F34ILL | General
F34ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (4) 36", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 36 | 4 | 25 | 86 | F34ILL-R | General
F34LL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (4) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 36 | 4 | 25 | 89 | F34LL | General
F34LL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (4) 36", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 36 | 4 | 25 | 84 | F34LL-R | General
F36ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (6) 36", T-8 lamp, Instant Start Ballast, RLO (BF<.85) | Electronic | 36 | 6 | 25 | 134 | F36ILL-R | General
F41ILL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 1 | 32 | 31 | F41ILL | General
F41SILL | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 1 | 30 | 28 | F41SILL | General
F41SILL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 30 | 27 | F41SILL/T2 | General
F41SILL/T3 | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 48 | 1 | 30 | 27 | F41SILL/T3 | General
F41SILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 48 | 1 | 30 | 26 | F41SILL/T4 | General
F41SILL-R | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 1 | 30 | 25 | F41SILL-R | General
F41SILL/T2-R | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 30 | 24 | F41SILL/T2-R | General
F41SILL/T3-R | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 3 Lamp Ballast | Electronic | 48 | 1 | 30 | 24 | F41SILL/T3-R | General
F41SILL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 48 | 1 | 30 | 23 | F41SILL/T4-R | General
F41SILL-H | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 48 | 1 | 30 | 37 | F41SILL-H | General
F41SILL/T2-H | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 30 | 36 | F41SILL/T2-H | General
F41SILL/T3-H | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1), Tandem 3 Lamp Ballast | Electronic | 48 | 1 | 30 | 36 | F41SILL/T3-H | General
F41SSILL | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 1 | 28 | 26 | F41SSILL | General
F41SSILL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 28 | 25 | F41SSILL/T2 | General
F41SSILL/T3 | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 48 | 1 | 28 | 25 | F41SSILL/T3 | General
F41SSILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 48 | 1 | 28 | 24 | F41SSILL/T4 | General
F41SSILL-R | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 1 | 28 | 23 | F41SSILL-R | General
F41SSILL/T2-R | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 28 | 22 | F41SSILL/T2-R | General
F41SSILL/T3-R | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 3 Lamp Ballast | Electronic | 48 | 1 | 28 | 22 | F41SSILL/T3-R | General
F41SSILL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 48 | 1 | 28 | 21 | F41SSILL/T4-R | General
F41SSILL-H | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 48 | 1 | 28 | 33 | F41SSILL-H | General
F41SSILL/T2-H | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 28 | 32 | F41SSILL/T2-H | General
F41SSILL/T3-H | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1), Tandem 3 Lamp Ballast | Electronic | 48 | 1 | 28 | 32 | F41SSILL/T3-H | General
F41ILL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 32 | 30 | F41ILL/T2 | General
F41ILL/T2-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 32 | 33 | F41ILL/T2-H | General
F41ILL/T2-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 32 | 26 | F41ILL/T2-R | General
F41ILL/T3 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 48 | 1 | 32 | 30 | F41ILL/T3 | General
F41ILL/T3-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1), Tandem 3 Lamp Ballast | Electronic | 48 | 1 | 32 | 31 | F41ILL/T3-H | General
F41ILL/T3-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 3 Lamp Ballast | Electronic | 48 | 1 | 32 | 26 | F41ILL/T3-R | General
F41ILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 48 | 1 | 32 | 28 | F41ILL/T4 | General
F41ILL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 48 | 1 | 32 | 26 | F41ILL/T4-R | General
F41ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 48 | 1 | 32 | 36 | F41ILL-H | General
F41LE | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp | Mag-ES | 48 | 1 | 32 | 35 | F41LE | General
F41LL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 1 | 32 | 32 | F41LL | General
F41LL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 32 | 30 | F41LL/T2 | General
F41LL/T2-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 32 | 39 | F41LL/T2-H | General
F41LL/T2-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 32 | 27 | F41LL/T2-R | General
F41LL/T3 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 48 | 1 | 32 | 31 | F41LL/T3 | General
F41LL/T3-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1), Tandem 3 Lamp Ballast | Electronic | 48 | 1 | 32 | 33 | F41LL/T3-H | General
F41LL/T3-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85), Tandem 3 Lamp Ballast | Electronic | 48 | 1 | 32 | 25 | F41LL/T3-R | General
F41LL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 48 | 1 | 32 | 30 | F41LL/T4 | General
F41LL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 48 | 1 | 32 | 26 | F41LL/T4-R | General
F41LL-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1) | Electronic | 48 | 1 | 32 | 39 | F41LL-H | General
F41LL-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 48 | 1 | 32 | 27 | F41LL-R | General
F41RSILL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 1 | 25 | 22 | F41RSILL | General
F41RSILL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 25 | 22 | F41RSILL/T2 | General
F41RSILL/T3 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 48 | 1 | 25 | 22 | F41RSILL/T3 | General
F41RSILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 48 | 1 | 25 | 22 | F41RSILL/T4 | General
F41RSILL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 1 | 25 | 20 | F41RSILL-R | General
F41RSILL-R/T2 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, RLO (BF<0.85), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 25 | 19 | F41RSILL-R/T2 | General
F41RSILL-R/T3 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, RLO (BF<0.85), Tandem 3 Lamp Ballast | Electronic | 48 | 1 | 25 | 19 | F41RSILL-R/T3 | General
F41RSILL-R/T4 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 48 | 1 | 25 | 19 | F41RSILL-R/T4 | General
F41RSILL-H | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, HLO (BF:.96 - 1.2) | Electronic | 48 | 1 | 25 | 30 | F41RSILL-H | General
F41RSILL-H/T2 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, HLO (BF:.96 - 1.2), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 25 | 30 | F41RSILL-H/T2 | General
F41RSILL-H/T3 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, HLO (BF:.96 - 1.2), Tandem 3 Lamp Ballast | Electronic | 48 | 1 | 25 | 30 | F41RSILL-H/T3 | General
F41RSILL-H/T4 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, HLO (BF:.96 - 1.2), Tandem 4 Lamp Ballast | Electronic | 48 | 1 | 25 | 29 | F41RSILL-H/T4 | General
F42ILL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 2 | 32 | 59 | F42ILL | General
F42SILL | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 2 | 30 | 53 | F42SILL | General
F42SILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 48 | 2 | 30 | 52 | F42SILL/T4 | General
F42SILL-R | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 2 | 30 | 47 | F42SILL-R | General
F42SILL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (2) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 48 | 2 | 30 | 46 | F42SILL/T4-R | General
F42SILL-H | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-2.2) | Electronic | 48 | 2 | 30 | 72 | F42SILL-H | General
F42SSILL | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 2 | 28 | 48 | F42SSILL | General
F42SSILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 48 | 2 | 28 | 47 | F42SSILL/T4 | General
F42SSILL-R | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 2 | 28 | 45 | F42SSILL-R | General
F42SSILL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (2) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 48 | 2 | 28 | 44 | F42SSILL/T4-R | General
F42SSILL-H | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-2.2) | Electronic | 48 | 2 | 28 | 67 | F42SSILL-H | General
F42ILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 48 | 2 | 32 | 56 | F42ILL/T4 | General
F42ILL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 48 | 2 | 32 | 51 | F42ILL/T4-R | General
F42ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 48 | 2 | 32 | 65 | F42ILL-H | General
F42ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 2 | 32 | 52 | F42ILL-R | General
F42ILL-V | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, VHLO (BF>1.1) | Electronic | 48 | 2 | 32 | 79 | F42ILL-V | General
F42LE | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp | Mag-ES | 48 | 2 | 32 | 71 | F42LE | General
F42LL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 2 | 32 | 60 | F42LL | General
F42LL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 48 | 2 | 32 | 59 | F42LL/T4 | General
F42LL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 48 | 2 | 32 | 53 | F42LL/T4-R | General
F42LL-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1) | Electronic | 48 | 2 | 32 | 70 | F42LL-H | General
F42LL-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 48 | 2 | 32 | 54 | F42LL-R | General
F42LL-V | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, VHLO (BF>1.1) | Electronic | 48 | 2 | 32 | 85 | F42LL-V | General
F42RSILL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 48", 25W T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 2 | 25 | 43 | F42RSILL | General
F42RSILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 48", 25W T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 48 | 2 | 25 | 43 | F42RSILL/T4 | General
F42RSILL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 48", 25W T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 2 | 25 | 38 | F42RSILL-R | General
F42RSILL-R/T4 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 48", 25W T-8 lamp, Instant Start Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 48 | 2 | 25 | 38 | F42RSILL-R/T4 | General
F42RSILL-H | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 48", 25W T-8 lamp, Instant Start Ballast, HLO (BF:.96 - 1.2) | Electronic | 48 | 2 | 25 | 58 | F42RSILL-H | General
F42RSILL-H/T4 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 48", 25W T-8 lamp, Instant Start Ballast, HLO (BF:.96 - 1.2), Tandem 4 Lamp Ballast | Electronic | 48 | 2 | 25 | 58 | F42RSILL-H/T4 | General
F43ILL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (3) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 3 | 32 | 89 | F43ILL | General
F43SILL | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (3) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 3 | 30 | 78 | F43SILL | General
F43SILL-R | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (3) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 3 | 30 | 70 | F43SILL-R | General
F43SILL-H | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (3) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-3.3) | Electronic | 48 | 3 | 30 | 105 | F43SILL-H | General
F43SSILL | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (3) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 3 | 28 | 72 | F43SSILL | General
F43SSILL-R | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (3) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 3 | 28 | 66 | F43SSILL-R | General
F43SSILL-H | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (3) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-3.3) | Electronic | 48 | 3 | 28 | 98 | F43SSILL-H | General
F43ILL/2 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (3) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), (2) ballast | Electronic | 48 | 3 | 32 | 90 | F43ILL/2 | General
F43ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (3) 48", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 48 | 3 | 32 | 93 | F43ILL-H | General
F43ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (3) 48", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 3 | 32 | 78 | F43ILL-R | General
F43ILL-V | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (3) 48", T-8 lamp, Instant Start Ballast, VHLO (BF>1.1) | Electronic | 48 | 3 | 32 | 112 | F43ILL-V | General
F43LE | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (3) 48", T-8 lamp | Mag-ES | 48 | 3 | 32 | 110 | F43LE | General
F43LL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (3) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 3 | 32 | 93 | F43LL | General
F43LL/2 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (3) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), (2) ballast | Electronic | 48 | 3 | 32 | 92 | F43LL/2 | General
F43LL-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (3) 48", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1) | Electronic | 48 | 3 | 32 | 98 | F43LL-H | General
F43LL-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (3) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 48 | 3 | 32 | 76 | F43LL-R | General
F43RSILL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (3) 48", 25W T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 3 | 25 | 65 | F43RSILL | General
F43RSILL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (3) 48", 25W T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 3 | 25 | 57 | F43RSILL-R | General
F43RSILL-H | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (3) 48", 25W T-8 lamp, Instant Start Ballast, HLO (BF:.96 - 1.2) | Electronic | 48 | 3 | 25 | 87 | F43RSILL-H | General
F44ILL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (4) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 4 | 32 | 112 | F44ILL | General
F44ILL-V | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (4) 48", T-8 lamp, Instant Start Ballast, VHLO (BF>1.1) | Electronic | 48 | 4 | 32 | 151 | F44ILL-V | General
F44SILL | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (4) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 4 | 30 | 105 | F44SILL | General
F44SILL-R | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (4) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 4 | 30 | 91 | F44SILL-R | General
F44SILL-H | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (4) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-4.4) | Electronic | 48 | 4 | 30 | 140 | F44SILL-H | General
F44SSILL | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (4) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 4 | 28 | 96 | F44SSILL | General
F44SSILL-R | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (4) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 4 | 28 | 86 | F44SSILL-R | General
F44SSILL-H | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (4) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-4.4) | Electronic | 48 | 4 | 28 | 131 | F44SSILL-H | General
F44ILL/2 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (4) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), (2) ballast | Electronic | 48 | 4 | 32 | 118 | F44ILL/2 | General
F44ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (4) 48", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 4 | 32 | 102 | F44ILL-R | General
F44LE | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (4) 48", T-8 lamp | Mag-ES | 48 | 4 | 32 | 142 | F44LE | General
F44LL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (4) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 4 | 32 | 118 | F44LL | General
F44LL/2 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (4) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), (2) ballast | Electronic | 48 | 4 | 32 | 120 | F44LL/2 | General
F44LL-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (4) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 48 | 4 | 32 | 105 | F44LL-R | General
F44ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (4) 48", T-8 lamp, Instant Start Ballast, HLO (BF: .96-1.2) | Electronic | 48 | 4 | 32 | 144 | F44ILL-H | General
F44RSILL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (4) 48", 25W T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 4 | 25 | 85 | F44RSILL | General
F44RSILL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (4) 48", 25W T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 4 | 25 | 76 | F44RSILL-R | General
F44RSILL-H | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (4) 48", 25W T-8 lamp, Instant Start Ballast, HLO (BF:.96 - 1.2) | Electronic | 48 | 4 | 25 | 112 | F44RSILL-H | General
F45ILL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (5) 48", T-8 lamp, (1) 3-lamp IS ballast and (1) 2-lamp IS ballast, NLO (BF: .85-.95) | Electronic | 48 | 5 | 32 | 148 | F45ILL | General
F46ILL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (6) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 6 | 32 | 175 | F46ILL | General
F46ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (6) 48", T-8 lamp, Instant Start Ballast, RLO (BF< .85) | Electronic | 48 | 6 | 32 | 156 | F46ILL-R | General
F46LL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (6) 48", T-8 lamp, NLO (BF: .85-.95) | Electronic | 48 | 6 | 32 | 182 | F46LL | General
F46ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (6) 48", T-8 lamp, Instant Start Ballast, HLO (BF: .96-1.2) | Electronic | 48 | 6 | 32 | 222 | F46ILL-H | General
F46ILL-V | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (6) 48", T-8 lamp, Instant Start Ballast, VLO (BF: >1.2) | Electronic | 48 | 6 | 32 | 255 | F46ILL-V | General
F46SIL | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (6) 48", 30W T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 6 | 32 | 158 | F46SIL | General
F46SSIL | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (6) 48", 28W T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 6 | 32 | 144 | F46SSIL | General
F48ILL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (8) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 8 | 32 | 224 | F48ILL | General
F48ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (8) 48", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 8 | 32 | 204 | F48ILL-R | General
F48LHL | Linear Fluorescent | T8 Linear Fluorescent | F48T8/HO | Fluorescent, (8) 48", T-8 HO lamp, NLO (BF: 0.95), 4 Ballasts | Electronic | 48 | 8 | 44 | 392 | F48LHL | General
F410GHL | Linear Fluorescent | T8 Linear Fluorescent | F48T5/HO | Fluorescent, (10) 48", STD HO T5 lamp | Electronic | 48 | 10 | 54 | 588 | F410GHL | General
F412GHL | Linear Fluorescent | T8 Linear Fluorescent | F48T5/HO | Fluorescent, (12) 48", STD HO T5 lamp | Electronic | 48 | 12 | 54 | 702 | F412GHL | General
F51ILL | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (1) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 60 | 1 | 40 | 36 | F51ILL | General
F51ILL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (1) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 60 | 1 | 40 | 36 | F51ILL/T2 | General
F51ILL/T3 | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (1) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 60 | 1 | 40 | 35 | F51ILL/T3 | General
F51ILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (1) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 60 | 1 | 40 | 34 | F51ILL/T4 | General
F51ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (1) 60", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 60 | 1 | 40 | 43 | F51ILL-R | General
F52ILL | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (2) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 60 | 2 | 40 | 72 | F52ILL | General
F52ILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (2) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 60 | 2 | 40 | 67 | F52ILL/T4 | General
F52ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (2) 60", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 60 | 2 | 40 | 80 | F52ILL-H | General
F52ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (2) 60", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 60 | 2 | 40 | 73 | F52ILL-R | General
F53ILL | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (3) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 60 | 3 | 40 | 106 | F53ILL | General
F53ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (3) 60", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 60 | 3 | 40 | 108 | F53ILL-H | General
F54ILL | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (4) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 60 | 4 | 40 | 134 | F54ILL | General
F54ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (4) 60", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 60 | 4 | 40 | 126 | F54ILL-H | General
F62ILHL | Linear Fluorescent | T8 Linear Fluorescent | F72T8 | Fluorescent, (2) 72", T-8 HO lamp, Instant Start Ballast | Electronic | 72 | 2 | 65 | 147 | F62ILHL | General
F81ILL | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 96 | 1 | 59 | 58 | F81ILL | General
F81ILL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 96 | 1 | 59 | 55 | F81ILL/T2 | General
F81ILL/T2-R | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 2 Lamp Ballast | Electronic | 96 | 1 | 59 | 49 | F81ILL/T2-R | General
F81ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 96 | 1 | 59 | 68 | F81ILL-H | General
F81ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 96 | 1 | 59 | 57 | F81ILL-R | General
F81ILL-V | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, VHLO (BF>1.1) | Electronic | 96 | 1 | 59 | 71 | F81ILL-V | General
F81LHL | Linear Fluorescent | T8 Linear Fluorescent | F96T8/HO | Fluorescent, (1) 96", T8 HO lamp | Electronic | 96 | 1 | 86 | 85 | F81LHL | General
F81LHL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F96T8/HO | Fluorescent, (1) 96", T8 HO lamp, tandem wired to 2-lamp ballast | Electronic | 96 | 1 | 86 | 80 | F81LHL/T2 | General
F82ILL | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (2) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 96 | 2 | 59 | 109 | F82ILL | General
F82ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (2) 96", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 96 | 2 | 59 | 98 | F82ILL-R | General
F82LHL | Linear Fluorescent | T8 Linear Fluorescent | F96T8/HO | Fluorescent, (2) 96", T8 HO lamp | Electronic | 96 | 2 | 86 | 160 | F82LHL | General
F83ILL | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (3) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 96 | 3 | 59 | 167 | F83ILL | General
F84ILL | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (4) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 96 | 4 | 59 | 219 | F84ILL | General
F84LHL | Linear Fluorescent | T8 Linear Fluorescent | F96T8/HO | Fluorescent, (4) 96", T8 HO lamp | Electronic | 96 | 4 | 86 | 320 | F84LHL | General
F86ILL | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (6) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 96 | 6 | 59 | 328 | F86ILL | General
F21GL | Linear Fluorescent | T5 Linear Fluorescent | F24T5 | Fluorescent, (1) 24", STD T5 lamp | Electronic | 24 | 1 | 14 | 18 | F21GL | General
F21GHL | Linear Fluorescent | T5 Linear Fluorescent | F24T5/HO | Fluorescent, (1) 24", STD HO T5 lamp | Electronic | 24 | 1 | 24 | 29 | F21GHL | General
F22GHL | Linear Fluorescent | T5 Linear Fluorescent | F24T5/HO | Fluorescent, (2) 24", STD HO T5 lamp | Electronic | 24 | 2 | 24 | 55 | F22GHL | General
F22GL | Linear Fluorescent | T5 Linear Fluorescent | F24T5 | Fluorescent, (2) 24", STD T5 lamp | Electronic | 24 | 2 | 14 | 35 | F22GL | General
F31GHL | Linear Fluorescent | T5 Linear Fluorescent | F36T5/HO | Fluorescent, (1) 36", STD HO T5 lamp | Electronic | 36 | 1 | 39 | 43 | F31GHL | General
F31GL | Linear Fluorescent | T5 Linear Fluorescent | F36T5 | Fluorescent, (1) 36", STD T5 lamp | Electronic | 36 | 1 | 21 | 27 | F31GL | General
F32GHL | Linear Fluorescent | T5 Linear Fluorescent | F36T5/HO | Fluorescent, (2) 36", STD HO T5 lamp | Electronic | 36 | 2 | 39 | 85 | F32GHL | General
F32SHS | Linear Fluorescent | T5 Linear Fluorescent | F36T12/HO | Fluorescent, (2) 36", HO, lamp | Mag-STD | 36 | 2 | 50 | 114 | F32SHS | General
F32GL | Linear Fluorescent | T5 Linear Fluorescent | F36T5 | Fluorescent, (1) 36", STD T5 lamp | Electronic | 36 | 2 | 21 | 52 | F32GL | General
F41GHL | Linear Fluorescent | T5 Linear Fluorescent | F48T5/HO | Fluorescent, (1) 48", STD HO T5 lamp | Electronic | 48 | 1 | 54 | 59 | F41GHL | General
F41GL | Linear Fluorescent | T5 Linear Fluorescent | F48T5 | Fluorescent, (1) 48", STD T5 lamp | Electronic | 48 | 1 | 28 | 32 | F41GL | General
F41GHL-H | Linear Fluorescent | T5 Linear Fluorescent | F54T5/HO | Fluorescent, (1) 48", STD HO T5 lamp HLO (BF: .96-1.2) | Electronic | 48 | 1 | 54 | 62 | F41GHL-H | General
F42GHL | Linear Fluorescent | T5 Linear Fluorescent | F48T5/HO | Fluorescent, (2) 48", STD HO T5 lamp | Electronic | 48 | 2 | 54 | 117 | F42GHL | General
F42GHL-H | Linear Fluorescent | T5 Linear Fluorescent | F54T5/HO | Fluorescent, (2) 48", STD HO T5 lamp HLO (BF: .96-1.2) | Electronic | 48 | 2 | 54 | 118 | F42GHL-H | General
F43GHL | Linear Fluorescent | T5 Linear Fluorescent | F48T5/HO | Fluorescent, (3) 48", STD HO T5 lamp | Electronic | 48 | 3 | 54 | 177 | F43GHL | General
F43GHL-H | Linear Fluorescent | T5 Linear Fluorescent | F54T5/HO | Fluorescent, (3) 48", STD HO T5 lamp HLO (BF: .96-1.2) | Electronic | 48 | 3 | 54 | 182 | F43GHL-H | General
F44GHL | Linear Fluorescent | T5 Linear Fluorescent | F48T5/HO | Fluorescent, (4) 48", STD HO T5 lamp | Electronic | 48 | 4 | 54 | 234 | F44GHL | General
F44GHL-H | Linear Fluorescent | T5 Linear Fluorescent | F54T5/HO | Fluorescent, (4) 48", STD HO T5 lamp HLO (BF: .96-1.2) | Electronic | 48 | 4 | 54 | 240 | F44GHL-H | General
F45GHL | Linear Fluorescent | T5 Linear Fluorescent | F48T5/HO | Fluorescent, (5) 48", STD HO T5 lamp | Electronic | 48 | 5 | 54 | 294 | F45GHL | General
F46GHL | Linear Fluorescent | T5 Linear Fluorescent | F48T5/HO | Fluorescent, (6) 48", STD HO T5 lamp | Electronic | 48 | 6 | 54 | 351 | F46GHL | General
F46GHL-H | Linear Fluorescent | T5 Linear Fluorescent | F54T5/HO | Fluorescent, (6) 48", STD HO T5 lamp HLO (BF: .96-1.2) | Electronic | 48 | 6 | 54 | 364 | F46GHL-H | General
F48GHL | Linear Fluorescent | T5 Linear Fluorescent | F48T5/HO | Fluorescent, (8) 48", STD HO T5 lamp | Electronic | 48 | 8 | 54 | 468 | F48GHL | General
F51GHL | Linear Fluorescent | T5 Linear Fluorescent | F60T5/HO | Fluorescent, (1) 60", STD HO T5 lamp | Electronic | 60 | 1 | 80 | 89 | F51GHL | General
F51GL | Linear Fluorescent | T5 Linear Fluorescent | F60T5 | Fluorescent, (1) 60", STD T5 lamp | Electronic | 60 | 1 | 35 | 39 | F51GL | General
F52GL | Linear Fluorescent | T5 Linear Fluorescent | F60T5 | Fluorescent, (2) 60", STD T5 lamp | Electronic | 60 | 2 | 35 | 76 | F52GL | General
F1.51SS | Linear Fluorescent | T12 Linear Fluorescent | F15T12 | Fluorescent, (1) 18" T12 lamp | Mag-STD | 12 | 1 | 15 | 19 | F1.51LS | General
F1.52SS | Linear Fluorescent | T12 Linear Fluorescent | F15T12 | Fluorescent, (2) 18", T12 lamp | Mag-STD | 12 | 2 | 15 | 36 | F1.52LS | General
F21HS | Linear Fluorescent | T12 Linear Fluorescent | F24T12/HO | Fluorescent, (1) 24", HO lamp | Mag-STD | 24 | 1 | 35 | 62 | F21ILL | General
F21SE | Linear Fluorescent | T12 Linear Fluorescent | F20T12 | Fluorescent, (1) 24", STD lamp | Mag-ES | 24 | 1 | 20 | 26 | F21ILL | General
F21SS | Linear Fluorescent | T12 Linear Fluorescent | F20T12 | Fluorescent, (1) 24", STD lamp | Mag-STD | 24 | 1 | 20 | 28 | F21ILL | General
F22SHS | Linear Fluorescent | T12 Linear Fluorescent | F24T12/HO | Fluorescent, (2) 24", HO lamp | Mag-STD | 24 | 2 | 35 | 90 | F22ILL | General
F22SE | Linear Fluorescent | T12 Linear Fluorescent | F20T12 | Fluorescent, (2) 24", STD lamp | Mag-ES | 24 | 2 | 20 | 51 | F22ILL | General
F22SS | Linear Fluorescent | T12 Linear Fluorescent | F20T12 | Fluorescent, (2) 24", STD lamp | Mag-STD | 24 | 2 | 20 | 56 | F22ILL | General
F23SE | Linear Fluorescent | T12 Linear Fluorescent | F20T12 | Fluorescent, (3) 24", STD lamp | Mag-ES | 24 | 3 | 20 | 77 | F23ILL | General
F23SS | Linear Fluorescent | T12 Linear Fluorescent | F20T12 | Fluorescent, (3) 24", STD lamp | Mag-STD | 24 | 3 | 20 | 84 | F23ILL | General
F24SE | Linear Fluorescent | T12 Linear Fluorescent | F20T12 | Fluorescent, (4) 24", STD lamp | Mag-ES | 24 | 4 | 20 | 102 | F24ILL | General
F24SS | Linear Fluorescent | T12 Linear Fluorescent | F20T12 | Fluorescent, (4) 24", STD lamp | Mag-STD | 24 | 4 | 20 | 112 | F24ILL | General
F26SE | Linear Fluorescent | T12 Linear Fluorescent | F20T12 | Fluorescent, (6) 24", STD lamp | Mag-ES | 24 | 6 | 20 | 153 | F26ILL | General
F26SS | Linear Fluorescent | T12 Linear Fluorescent | F20T12 | Fluorescent, (6) 24", STD lamp | Mag-STD | 24 | 6 | 20 | 168 | F26ILL | General
F31EE | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (1) 36", ES lamp | Mag-ES | 36 | 1 | 25 | 38 | F31ILL | General
F31EE/T2 | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (1) 36", ES lamp, Tandem wired | Mag-ES | 36 | 1 | 25 | 33 | F31ILL | General
F31EL | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (1) 36", ES lamp | Electronic | 36 | 1 | 25 | 26 | F31ILL | General
F31ES | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (1) 36", ES lamp | Mag-STD | 36 | 1 | 25 | 42 | F31ILL | General
F31ES/T2 | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (1) 36", ES lamp, Tandem wired | Mag-STD | 36 | 1 | 25 | 37 | F31ILL | General
F31SE/T2 | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (1) 36", STD lamp, Tandem wired | Mag-ES | 36 | 1 | 30 | 37 | F31ILL | General
F31SHS | Linear Fluorescent | T12 Linear Fluorescent | F36T12/HO | Fluorescent, (1) 36", HO lamp | Mag-STD | 36 | 1 | 50 | 70 | F31ILL | General
F31SL | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (1) 36", STD lamp | Electronic | 36 | 1 | 30 | 31 | F31ILL | General
F31SS | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (1) 36", STD lamp | Mag-STD | 36 | 1 | 30 | 46 | F31ILL | General
F31SS/T2 | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (1) 36", STD lamp, Tandem wired | Mag-STD | 36 | 1 | 30 | 41 | F31ILL | General
F32EE | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (2) 36", ES lamp | Mag-ES | 36 | 2 | 25 | 66 | F32ILL | General
F32EL | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (2) 36", ES lamp | Electronic | 36 | 2 | 25 | 50 | F32ILL | General
F32ES | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (2) 36", ES lamp | Mag-STD | 36 | 2 | 25 | 73 | F32ILL | General
F32SE | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (2) 36", STD lamp | Mag-ES | 36 | 2 | 30 | 74 | F32ILL | General
F32SL | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (2) 36", STD lamp | Electronic | 36 | 2 | 30 | 58 | F32ILL | General
F32SS | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (2) 36", STD lamp | Mag-STD | 36 | 2 | 30 | 81 | F32ILL | General
F33EE | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (3) 36", ES lamp | Mag-ES | 36 | 3 | 25 | 104 | F33ILL | General
F33EL | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (3) 36", ES lamp | Electronic | 36 | 3 | 25 | 76 | F33ILL | General
F33ES | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (3) 36", ES lamp | Mag-STD | 36 | 3 | 25 | 115 | F33ILL | General
F33SE | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (3) 36", STD lamp, (1) STD ballast and (1) ES ballast | Mag-ES | 36 | 3 | 30 | 120 | F33ILL | General
F33SS | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (3) 36", STD lamp | Mag-STD | 36 | 3 | 30 | 127 | F33ILL | General
F34EE | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (4) 36", ES lamp | Mag-ES | 36 | 4 | 25 | 132 | F34ILL | General
F34EL | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (4) 36", ES lamp | Electronic | 36 | 4 | 25 | 100 | F34ILL | General
F34SE | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (4) 36", STD lamp | Mag-ES | 36 | 4 | 30 | 148 | F34ILL | General
F34SL | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (4) 36", STD lamp | Electronic | 36 | 4 | 30 | 116 | F34ILL | General
F34SS | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (4) 36", STD lamp | Mag-STD | 36 | 4 | 30 | 162 | F34ILL | General
F36EE | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (6) 36", ES lamp | Mag-ES | 36 | 6 | 25 | 198 | F36ILL | General
F36SE | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (6) 36", STD lamp | Mag-ES | 36 | 6 | 30 | 238 | F36ILL | General
F41EE | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (1) 48", ES lamp | Mag-ES | 48 | 1 | 34 | 43 | F41ILL | General
F41EE/D2 | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (1) 48", ES lamp, 2 ballast | Mag-ES | 48 | 1 | 34 | 43 | F41ILL | General
F41EE/T2 | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (1) 48", ES lamp, tandem wired, 2-lamp ballast | Mag-ES | 48 | 1 | 34 | 36 | F41ILL | General
F41EHS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/HO/ES | Fluorescent, (1) 48", ES HO lamp | Mag-STD | 48 | 1 | 55 | 80 | F41ILL | General
F41EIS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/ES | Fluorescent, (1) 48" ES Instant Start lamp. Magnetic ballast | Mag-STD | 48 | 1 | 30 | 51 | F41ILL | General
F41EL | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (1) 48", T12 ES lamp, Electronic Ballast | Electronic | 48 | 1 | 34 | 32 | F41ILL | General
F41EL/T2 | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (1) 48", T-12 ES lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 34 | 32 | F41ILL | General
F41ES | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (1) 48", ES lamp | Mag-STD | 48 | 1 | 34 | 50 | F41ILL | General
F41EVS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/VHO/ES | Fluorescent, (1) 48", VHO ES lamp | Mag-STD | 48 | 1 |  | 123 | F41ILL | General
F41IAL | Linear Fluorescent | T12 Linear Fluorescent | F25T12 | Fluorescent, (1) 48", F25T12 lamp, Instant Start Ballast | Electronic | 48 | 1 | 25 | 25 | F41ILL | General
F41IAL/T2-R | Linear Fluorescent | T12 Linear Fluorescent | F25T12 | Fluorescent, (1) 48", F25T12 lamp, Instant Start, Tandem 2-Lamp Ballast, RLO (BF<0.85) | Electronic | 48 | 1 | 25 | 19 | F41ILL | General
F41IAL/T3-R | Linear Fluorescent | T12 Linear Fluorescent | F25T12 | Fluorescent, (1) 48", F25T12 lamp, Instant Start, Tandem 3-Lamp Ballast, RLO (BF<0.85) | Electronic | 48 | 1 | 25 | 20 | F41ILL | General
F41SE | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (1) 48", STD lamp | Mag-ES | 48 | 1 | 40 | 50 | F41ILL | General
F41SHS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/HO | Fluorescent, (1) 48", STD HO lamp | Mag-STD | 48 | 1 | 60 | 85 | F41ILL | General
F41SIL | Linear Fluorescent | T12 Linear Fluorescent | F48T12 | Fluorescent, (1) 48", STD IS lamp, Electronic ballast | Electronic | 48 | 1 | 39 | 46 | F41ILL | General
F41SIL/T2 | Linear Fluorescent | T12 Linear Fluorescent | F48T12 | Fluorescent, (1) 48", STD IS lamp, Electronic ballast, tandem wired | Electronic | 48 | 1 | 39 | 37 | F41ILL | General
F41SIS | Linear Fluorescent | T12 Linear Fluorescent | F48T12 | Fluorescent, (1) 48", STD IS lamp | Mag-STD | 48 | 1 | 39 | 60 | F41ILL | General
F41SIS/T2 | Linear Fluorescent | T12 Linear Fluorescent | F48T12 | Fluorescent, (1) 48", STD IS lamp, tandem to 2-lamp ballast | Mag-STD | 48 | 1 | 39 | 52 | F41ILL | General
F41SL/T2 | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (1) 48", T-12 STD lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 40 | 36 | F41ILL | General
F41SS | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (1) 48", STD lamp | Mag-STD | 48 | 1 | 40 | 57 | F41ILL | General
F41SVS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/VHO | Fluorescent, (1) 48", STD VHO lamp | Mag-STD | 48 | 1 | 110 | 135 | F41ILL | General
F42EE | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (2) 48", ES lamp | Mag-ES | 48 | 2 | 34 | 72 | F42ILL | General
F42EE/D2 | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (2) 48", ES lamp, 2 Ballasts (delamped) | Mag-ES | 48 | 2 | 34 | 76 | F42ILL | General
F42EHS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/HO/ES | Fluorescent, (2) 42", HO lamp (3.5' lamp) | Mag-STD | 48 | 2 | 55 | 135 | F42ILL | General
F42EIS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/ES | Fluorescent, (2) 48" ES Instant Start lamp. Magnetic ballast | Mag-STD | 48 | 2 | 30 | 82 | F42ILL | General
F42EL | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (2) 48", T12 ES lamps, Electronic Ballast | Electronic | 48 | 2 | 34 | 60 | F42ILL | General
F42ES | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (2) 48", ES lamp | Mag-STD | 48 | 2 | 34 | 80 | F42ILL | General
F42EVS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/VHO/ES | Fluorescent, (2) 48", VHO ES lamp | Mag-STD | 48 | 2 |  | 210 | F42ILL | General
F42IAL/T4-R | Linear Fluorescent | T12 Linear Fluorescent | F25T12 | Fluorescent, (2) 48", F25T12 lamp, Instant Start, Tandem 4-Lamp Ballast, RLO (BF<0.85) | Electronic | 48 | 2 | 25 | 40 | F42ILL | General
F42IAL-R | Linear Fluorescent | T12 Linear Fluorescent | F25T12 | Fluorescent, (2) 48", F25T12 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 2 | 25 | 39 | F42ILL | General
F42SE | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (2) 48", STD lamp | Mag-ES | 48 | 2 | 40 | 86 | F42ILL | General
F42SHS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/HO | Fluorescent, (2) 48", STD HO lamp | Mag-STD | 48 | 2 | 60 | 145 | F42ILL | General
F42SIL | Linear Fluorescent | T12 Linear Fluorescent | F48T12 | Fluorescent, (2) 48", STD IS lamp, Electronic ballast | Electronic | 48 | 2 | 39 | 74 | F42ILL | General
F42SIS | Linear Fluorescent | T12 Linear Fluorescent | F48T12 | Fluorescent, (2) 48", STD IS lamp | Mag-STD | 48 | 2 | 39 | 103 | F42ILL | General
F42GL | Linear Fluorescent | T12 Linear Fluorescent | F48T5 | Fluorescent, (2) 48", STD T5 lamp | Electronic | 48 | 2 | 28 | 63 | F42ILL | General
F42SS | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (2) 48", STD lamp | Mag-STD | 48 | 2 | 40 | 94 | F42ILL | General
F42SVS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/VHO | Fluorescent, (2) 48", STD VHO lamp | Mag-STD | 48 | 2 | 110 | 242 | F42ILL | General
F43EE | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (3) 48", ES lamp | Mag-ES | 48 | 3 | 34 | 115 | F43ILL | General
F43EHS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/HO/ES | Fluorescent, (3) 48", ES HO lamp (3.5' lamp) | Mag-STD | 48 | 3 | 55 | 215 | F43ILL | General
F43EIS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/ES | Fluorescent, (3) 48" ES Instant Start lamp. Magnetic ballast | Mag-STD | 48 | 3 | 30 | 133 | F43ILL | General
F43EL | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (3) 48", T12 ES lamps, Electronic Ballast | Electronic | 48 | 3 | 34 | 92 | F43ILL | General
F43ES | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (3) 48", ES lamp | Mag-STD | 48 | 3 | 34 | 130 | F43ILL | General
F43EVS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/VHO/ES | Fluorescent, (3) 48", VHO ES lamp | Mag-STD | 48 | 3 |  | 333 | F43ILL | General
F43IAL-R | Linear Fluorescent | T12 Linear Fluorescent | F25T12 | Fluorescent, (3) 48", F25T12 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 3 | 25 | 60 | F43ILL | General
F43SE | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (3) 48", STD lamp | Mag-ES | 48 | 3 | 40 | 136 | F43ILL | General
F43SHS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/HO | Fluorescent, (3) 48", STD HO lamp | Mag-STD | 48 | 3 | 60 | 230 | F43ILL | General
F43SIL | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (3) 48", STD IS lamp, Electronic ballast | Electronic | 48 | 3 | 39 | 120 | F43ILL | General
F43SIS | Linear Fluorescent | T12 Linear Fluorescent | F48T12 | Fluorescent, (3) 48", STD IS lamp | Mag-STD | 48 | 3 | 39 | 162 | F43ILL | General
F43SS | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (3) 48", STD lamp | Mag-STD | 48 | 3 | 40 | 151 | F43ILL | General
F43SVS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/VHO | Fluorescent, (3) 48", STD VHO lamp | Mag-STD | 48 | 3 | 110 | 377 | F43ILL | General
F44EE | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (4) 48", ES lamp | Mag-ES | 48 | 4 | 34 | 144 | F44ILL | General
F44EE/D4 | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (4) 48", ES lamp, 4 Ballasts (delamped) | Mag-ES | 48 | 4 | 34 | 152 | F44ILL | General
F44EHS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/HO/ES | Fluorescent, (4) 48", ES HO lamp | Mag-STD | 48 | 4 | 55 | 270 | F44ILL | General
F44EIS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/ES | Fluorescent, (4) 48" ES Instant Start lamp, Magnetic ballast | Mag-STD | 48 | 4 | 30 | 164 | F44ILL | General
F44EL | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (4) 48", T12 ES lamp, Electronic Ballast | Electronic | 48 | 4 | 34 | 120 | F44ILL | General
F44ES | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (4) 48", ES lamp | Mag-STD | 48 | 4 | 34 | 160 | F44ILL | General
F44EVS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/VHO/ES | Fluorescent, (4) 48", VHO ES lamp | Mag-STD | 48 | 4 |  | 420 | F44ILL | General
F44IAL-R | Linear Fluorescent | T12 Linear Fluorescent | F25T12 | Fluorescent, (4) 48", F25T12 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 4 | 25 | 80 | F44ILL | General
F44SE | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (4) 48", STD lamp | Mag-ES | 48 | 4 | 40 | 172 | F44ILL | General
F44SHS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/HO | Fluorescent, (4) 48", STD HO lamp | Mag-STD | 48 | 4 | 60 | 290 | F44ILL | General
F44SIL | Linear Fluorescent | T12 Linear Fluorescent | F48T12 | Fluorescent, (4) 48", STD IS lamp, Electronic ballast | Electronic | 48 | 4 | 39 | 148 | F44ILL | General
F44SIS | Linear Fluorescent | T12 Linear Fluorescent | F48T12 | Fluorescent, (4) 48", STD IS lamp | Mag-STD | 48 | 4 | 39 | 204 | F44ILL | General
F44SS | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (4) 48", STD lamp | Mag-STD | 48 | 4 | 40 | 188 | F44ILL | General
F44SVS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/VHO | Fluorescent, (4) 48", STD VHO lamp | Mag-STD | 48 | 4 | 110 | 484 | F44ILL | General
F46EE | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (6) 48", ES lamp | Mag-ES | 48 | 6 | 34 | 216 | F46ILL | General
F46EL | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (6) 48", ES lamp | Electronic | 48 | 6 | 34 | 186 | F46ILL | General
F46ES | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (6) 48", ES lamp | Mag-STD | 48 | 6 | 34 | 236 | F46ILL | General
F46EHS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/HO/ES | Fluorescent, (6) 48", ES HO lamp (3.5' lamp) | Mag-STD | 48 | 6 | 55 | 405 | F46ILL | General
F46SE | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (6) 48", STD lamp | Mag-ES | 48 | 6 | 40 | 258 | F46ILL | General
F46SS | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (6) 48", STD lamp | Mag-STD | 48 | 6 | 40 | 282 | F46ILL | General
F48EE | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (8) 48", ES lamp | Mag-ES | 48 | 8 | 34 | 288 | F48ILL | General
F48EHS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/HO/ES | Fluorescent, (8) 48", ES HO lamp (3.5' lamp) | Mag-STD | 48 | 8 | 55 | 540 | F48ILL | General
F51ILHL | Linear Fluorescent | T8 Linear Fluorescent | F60T8/HO | Fluorescent, (1) 60", T-8 HO lamp, Instant Start Ballast | Electronic | 60 | 1 | 55 | 59 | N/A | General
F51SHE | Linear Fluorescent | T12 Linear Fluorescent | F60T12/HO | Fluorescent, (1) 60", STD HO lamp | Mag-ES | 60 | 1 | 75 | 88 | F51ILL | General
F51SHL | Linear Fluorescent | T12 Linear Fluorescent | F60T12/HO | Fluorescent, (1) 60", STD HO lamp | Electronic | 60 | 1 | 75 | 69 | F51ILL | General
F51SHS | Linear Fluorescent | T12 Linear Fluorescent | F60T12/HO | Fluorescent, (1) 60", STD HO lamp | Mag-STD | 60 | 1 | 75 | 92 | F51ILL | General
F51SL | Linear Fluorescent | T12 Linear Fluorescent | F60T12 | Fluorescent, (1) 60", STD lamp | Electronic | 60 | 1 | 50 | 44 | F51ILL | General
F51SS | Linear Fluorescent | T12 Linear Fluorescent | F60T12 | Fluorescent, (1) 60", STD lamp | Mag-STD | 60 | 1 | 50 | 63 | F51ILL | General
F51SVS | Linear Fluorescent | T12 Linear Fluorescent | F60T12/VHO | Fluorescent, (1) 60", VHO ES lamp | Mag-STD | 60 | 1 | 135 | 165 | F51ILL | General
F52ILHL | Linear Fluorescent | T8 Linear Fluorescent | F60T8/HO | Fluorescent, (2) 60", T-8 HO lamp, Instant Start Ballast | Electronic | 60 | 2 | 55 | 123 | N/A | General
F52SHE | Linear Fluorescent | T12 Linear Fluorescent | F60T12/HO | Fluorescent, (2) 60", STD HO lamp | Mag-ES | 60 | 2 | 75 | 176 | F52ILL | General
F52SHL | Linear Fluorescent | T12 Linear Fluorescent | F60T12/HO | Fluorescent, (2) 60", STD HO lamp | Electronic | 60 | 2 | 75 | 138 | F52ILL | General
F52SHS | Linear Fluorescent | T12 Linear Fluorescent | F60T12/HO | Fluorescent, (2) 60", STD HO lamp | Mag-STD | 60 | 2 | 75 | 168 | F52ILL | General
F52SL | Linear Fluorescent | T12 Linear Fluorescent | F60T12 | Fluorescent, (2) 60", STD lamp | Electronic | 60 | 2 | 50 | 88 | F52ILL | General
F52SS | Linear Fluorescent | T12 Linear Fluorescent | F60T12 | Fluorescent, (2) 60", STD lamp | Mag-STD | 60 | 2 | 50 | 128 | F52ILL | General
F52SVS | Linear Fluorescent | T12 Linear Fluorescent | F60T12/VHO | Fluorescent, (2) 60", VHO ES lamp | Mag-STD | 60 | 2 | 135 | 310 | F52ILL | General
F61ISL | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (1) 72", STD lamp, IS electronic ballast | Electronic | 72 | 1 | 55 | 68 | F61ILL | General
F61SE | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (1) 72", STD lamp | Mag-ES | 72 | 1 | 55 | 76 | F61ILL | General
F61SHS | Linear Fluorescent | T12 Linear Fluorescent | F72T12/HO | Fluorescent, (1) 72", STD HO lamp | Mag-STD | 72 | 1 | 85 | 120 | F61ILL | General
F61SS | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (1) 72", STD lamp | Mag-STD | 72 | 1 | 55 | 90 | F61ILL | General
F61SVS | Linear Fluorescent | T12 Linear Fluorescent | F72T12/VHO | Fluorescent, (1) 72", VHO lamp | Mag-STD | 72 | 1 | 160 | 180 | F61ILL | General
F62ISL | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (2) 72", STD lamp, IS electronic ballast | Electronic | 72 | 2 | 55 | 108 | F62ILL | General
F62SE | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (2) 72", STD lamp | Mag-ES | 72 | 2 | 55 | 122 | F62ILL | General
F62SHE | Linear Fluorescent | T12 Linear Fluorescent | F72T12/HO | Fluorescent, (2) 72", STD HO lamp | Mag-ES | 72 | 2 | 85 | 194 | F62ILL | General
F62SHS | Linear Fluorescent | T12 Linear Fluorescent | F72T12/HO | Fluorescent, (2) 72", STD HO lamp | Mag-STD | 72 | 2 | 85 | 220 | F62ILL | General
F62SL | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (2) 72", STD lamp | Electronic | 72 | 2 | 55 | 108 | F62ILL | General
F62SS | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (2) 72", STD lamp | Mag-STD | 72 | 2 | 55 | 145 | F62ILL | General
F62SVS | Linear Fluorescent | T12 Linear Fluorescent | F72T12/VHO | Fluorescent, (2) 72", VHO lamp | Mag-STD | 72 | 2 | 160 | 330 | F62ILL | General
F63ISL | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (3) 72", STD lamp, IS electronic ballast | Electronic | 72 | 3 | 55 | 176 | F63ILL | General
F63SS | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (3) 72", STD lamp | Mag-STD | 72 | 3 | 55 | 202 | F63ILL | General
F64ISL | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (4) 72", STD lamp, IS electronic ballast | Electronic | 72 | 4 | 55 | 216 | F64ILL | General
F64SE | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (4) 72", STD lamp | Mag-ES | 72 | 4 | 55 | 230 | F64ILL | General
F64SHE | Linear Fluorescent | T12 Linear Fluorescent | F72T12/HO | Fluorescent, (4) 72", STD HO lamp | Mag-ES | 72 | 4 | 85 | 388 | F64ILL | General
F64SS | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (4) 72", STD lamp | Mag-STD | 72 | 4 | 55 | 244 | F64ILL | General
F81EE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (1) 96", ES lamp | Mag-ES | 96 | 1 | 60 | 61 | F81ILL | General
F81EE/T2 | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (1) 96", ES lamp, tandem to 2-lamp ballast | Mag-ES | 96 | 1 | 60 | 62 | F81ILL | General
F81EHL | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (1) 96", ES HO lamp | Electronic | 96 | 1 | 95 | 80 | F81LHL | General
F81EHL/T2 | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (1) 96", ES HO lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 96 | 1 | 95 | 85 | F81LHL | General
F81EHS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (1) 96", ES HO lamp | Mag-STD | 96 | 1 | 95 | 125 | F81LHL | General
F81EL | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (1) 96", ES lamp | Electronic | 96 | 1 | 60 | 60 | F81ILL | General
F81EL/T2 | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (1) 96", ES lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 96 | 1 | 60 | 55 | F81ILL | General
F81ES | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (1) 96", ES lamp | Mag-STD | 96 | 1 | 60 | 83 | F81ILL | General
F81ES/T2 | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (1) 96", ES lamp, tandem to 2-lamp ballast | Mag-STD | 96 | 1 | 60 | 64 | F81ILL | General
F81EVS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/VHO/ES | Fluorescent, (1) 96", ES VHO lamp | Mag-STD | 96 | 1 | 185 | 200 | F81LHL | General
F81SE | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (1) 96", STD lamp | Mag-ES | 96 | 1 | 75 | 91 | F81ILL | General
F81SHE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO | Fluorescent, (1) 96", STD HO lamp | Mag-ES | 96 | 1 | 110 | 132 | F81LHL | General
F81SHL/T2 | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO | Fluorescent, (1) 96", STD HO lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 96 | 1 | 110 | 98 | F81LHL | General
F81SHS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO | Fluorescent, (1) 96", STD HO lamp | Mag-STD | 96 | 1 | 110 | 145 | F81LHL | General
F81SL | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (1) 96", STD lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 96 | 1 | 75 | 70 | F81ILL | General
F81SL/T2 | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (1) 96", STD lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 96 | 1 | 75 | 67 | F81ILL | General
F81SS | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (1) 96", STD lamp | Mag-STD | 96 | 1 | 75 | 100 | F81ILL | General
F81SVS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/VHO | Fluorescent, (1) 96", STD VHO lamp | Mag-STD | 96 | 1 | 215 | 230 | F81LHL | General
F82EE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (2) 96", ES lamp | Mag-ES | 96 | 2 | 60 | 123 | F82ILL | General
F82EHE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (2) 96", ES HO lamp | Mag-ES | 96 | 2 | 95 | 207 | F82LHL | General
F82EHL | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (2) 96", ES HO lamp | Electronic | 96 | 2 | 95 | 170 | F82LHL | General
F82EHS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (2) 96", ES HO lamp | Mag-STD | 96 | 2 | 95 | 227 | F82LHL | General
F82EL | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (2) 96", ES lamp | Electronic | 96 | 2 | 60 | 110 | F82ILL | General
F82ES | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (2) 96", ES lamp | Mag-STD | 96 | 2 | 60 | 138 | F82ILL | General
F82EVS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/VHO/ES | Fluorescent, (2) 96", ES VHO lamp | Mag-STD | 96 | 2 | 185 | 390 | F82LHL | General
F82SE | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (2) 96", STD lamp | Mag-ES | 96 | 2 | 75 | 158 | F82ILL | General
F82SHE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO | Fluorescent, (2) 96", STD HO lamp | Mag-ES | 96 | 2 | 110 | 237 | F82LHL | General
F82SHL | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO | Fluorescent, (2) 96", STD HO lamp | Electronic | 96 | 2 | 110 | 195 | F82LHL | General
F82SHS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO | Fluorescent, (2) 96", STD HO lamp | Mag-STD | 96 | 2 | 110 | 257 | F82LHL | General
F82SL | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (2) 96", STD lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 96 | 2 | 75 | 134 | F82ILL | General
F82SS | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (2) 96", STD lamp | Mag-STD | 96 | 2 | 75 | 173 | F82ILL | General
F82SVS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/VHO | Fluorescent, (2) 96", STD VHO lamp | Mag-STD | 96 | 2 | 215 | 450 | F82LHL | General
F83EE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (3) 96", ES lamp | Mag-ES | 96 | 3 | 60 | 210 | F83ILL | General
F83EHE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (3) 96", ES HO lamp, (1) 2-lamp ES Ballast, (1) 1-lamp STD Ballast | Mag-ES/STD | 96 | 3 | 95 | 319 | F83LHL | General
F83EHS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (3) 96", ES HO lamp | Mag-STD | 96 | 3 | 95 | 352 | F83LHL | General
F83EL | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (3) 96", ES lamp | Electronic | 96 | 3 | 60 | 179 | F83ILL | General
F83ES | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (3) 96", ES lamp | Mag-STD | 96 | 3 | 60 | 221 | F83ILL | General
F83EVS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/VHO/ES | Fluorescent, (3) 96", ES VHO lamp | Mag-STD | 96 | 3 | 185 | 590 | F83LHL | General
F83SHS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO | Fluorescent, (3) 96", STD HO lamp | Mag-STD | 96 | 3 | 110 | 392 | F83LHL | General
F83SS | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (3) 96", STD lamp | Mag-STD | 96 | 3 | 75 | 273 | F83ILL | General
F83SVS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/VHO | Fluorescent, (3) 96", STD VHO lamp | Mag-STD | 96 | 3 | 215 | 680 | F83LHL | General
F84EE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (4) 96", ES lamp | Mag-ES | 96 | 4 | 60 | 246 | F84ILL | General
F84EHE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (4) 96", ES HO lamp | Mag-ES | 96 | 4 | 95 | 414 | F84LHL | General
F84EHL | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (4) 96", ES HO lamp | Electronic | 96 | 4 | 95 | 340 | F84LHL | General
F84EHS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (4) 96", ES HO lamp | Mag-STD | 96 | 4 | 95 | 454 | F84LHL | General
F84EL | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (4) 96", ES lamp | Electronic | 96 | 4 | 60 | 220 | F84ILL | General
F84ES | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (4) 96", ES lamp | Mag-STD | 96 | 4 | 60 | 276 | F84ILL | General
F84EVS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/VHO/ES | Fluorescent, (4) 96", ES VHO lamp | Mag-STD | 96 | 4 | 185 | 780 | F84LHL | General
F84SE | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (4) 96", STD lamp | Mag-ES | 96 | 4 | 75 | 316 | F84ILL | General
F84SHE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO | Fluorescent, (4) 96", STD HO lamp | Mag-ES | 96 | 4 | 110 | 474 | F84LHL | General
F84SHL | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO | Fluorescent, (4) 96", STD HO lamp | Electronic | 96 | 4 | 110 | 390 | F84LHL | General
F84SHS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO | Fluorescent, (4) 96", STD HO lamp | Mag-STD | 96 | 4 | 110 | 514 | F84LHL | General
F84SL | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (4) 96", STD lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 96 | 4 | 75 | 268 | F84ILL | General
F84SS | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (4) 96", STD lamp | Mag-STD | 96 | 4 | 75 | 346 | F84ILL | General
F84SVS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/VHO | Fluorescent, (4) 96", STD VHO lamp | Mag-STD | 96 | 4 | 215 | 900 | F84LHL | General
F86EHS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (6) 96", ES HO lamp | Mag-STD | 96 | 6 | 95 | 721 | F86LHL | General
F86EE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (6) 96", ES lamp | Mag-ES | 96 | 6 | 60 | 369 | F86ILL | General
F86EL | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (6) 96", ES lamp | Electronic | 96 | 6 | 60 | 330 | F86ILL | General
F41TS | Linear Fluorescent | T10 Linear Fluorescent | F40T10 | Fluorescent, (1) 48", T-10 lamp | Mag-STD | 48 | 1 | 40 | 51 | F41ILL | General
FU1EE | U-Tube Fluorescent | U-Tube Fluorescent | FU40T12/ES | Fluorescent, (1) U-Tube, ES lamp | Mag-ES | 24 | 1 | 34 | 43 | FU1EE | General
FU1ILL | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (1) U-Tube, T-8 lamp, Instant Start ballast | Electronic | 24 | 1 | 32 | 31 | FU1ILL | General
FU1LL | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (1) U-Tube, T-8 lamp | Electronic | 24 | 1 | 32 | 32 | FU1LL | General
FU1LL-R | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (1) U-Tube, T-8 lamp, RLO (BF<0.85) | Electronic | 24 | 1 | 31 | 27 | FU1LL-R | General
FU2SS | U-Tube Fluorescent | U-Tube Fluorescent | FU40T12 | Fluorescent, (2) U-Tube, STD lamp | Mag-STD | 24 | 2 | 40 | 96 | FU2SS | General
FU2SE | U-Tube Fluorescent | U-Tube Fluorescent | FU40T12 | Fluorescent, (2) U-Tube, STD lamp | Mag-ES | 24 | 2 | 40 | 85 | FU2SE | General
FU2EE | U-Tube Fluorescent | U-Tube Fluorescent | FU40T12/ES | Fluorescent, (2) U-Tube, ES lamp | Mag-ES | 24 | 2 | 34 | 72 | FU2EE | General
FU2ES | U-Tube Fluorescent | U-Tube Fluorescent | FU40T12/ES | Fluorescent, (2) U-Tube, ES lamp | Mag-STD | 24 | 2 | 34 | 82 | FU2ES | General
FU2ILL | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, Instant Start Ballast | Electronic | 24 | 2 | 32 | 59 | FU2ILL | General
FU2ILL/T4 | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, Instant Start Ballast, tandem wired | Electronic | 24 | 2 | 32 | 56 | FU2ILL/T4 | General
FU2ILL/T4-R | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, Instant Start Ballast, RLO, tandem wired | Electronic | 24 | 2 | 32 | 51 | FU2ILL/T4-R | General
FU2ILL-H | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, Instant Start HLO Ballast | Electronic | 24 | 2 | 32 | 65 | FU2ILL-H | General
FU2ILL-R | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, Instant Start RLO Ballast | Electronic | 24 | 2 | 32 | 52 | FU2ILL-R | General
FU2LL | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp | Electronic | 24 | 2 | 32 | 60 | FU2LL | General
FU2LL/T2 | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, Tandem 4 lamp ballast | Electronic | 24 | 2 | 32 | 59 | FU2LL/T2 | General
FU2LL-R | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, RLO (BF<0.85) | Electronic | 24 | 2 | 31 | 54 | FU2LL-R | General
FU3EE | U-Tube Fluorescent | U-Tube Fluorescent | FU40T12/ES | Fluorescent, (3) U-Tube, ES lamp | Mag-ES | 24 | 3 | 35 | 115 | FU3EE | General
FU3ILL | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (3) U-Tube, T-8 lamp, Instant Start Ballast | Electronic | 24 | 3 | 32 | 89 | FU3ILL | General
FU3ILL-R | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (3) U-Tube, T-8 lamp, Instant Start RLO Ballast | Electronic | 24 | 3 | 32 | 78 | FU3ILL-R | General
FC12/1 | Circular Fluorescent | Circular Fluorescent | FC12T9 | Fluorescent, (1) 12" circular lamp, RS ballast | Mag-STD | 12 | 1 | 32 | 31 | FC12/1 | General
FC16/1 | Circular Fluorescent | Circular Fluorescent | FC16T9 | Fluorescent, (1) 16" circular lamp | Mag-STD | 16 | 1 | 40 | 35 | FC16/1 | General
FC20 | Circular Fluorescent | Circular Fluorescent | FC6T9 | Fluorescent, Circlite, (1) 20W lamp, Preheat ballast | Mag-STD |  | 1 | 20 | 20 | FC20 | General
FC22/1 | Circular Fluorescent | Circular Fluorescent | FC8T9 | Fluorescent, Circlite, (1) 22W lamp, preheat ballast | Mag-STD |  | 1 | 22 | 20 | FC22/1 | General
FC22/32/1 | Circular Fluorescent | Circular Fluorescent | FC22/32T9 | Fluorescent, Circlite, (1) 22W/32W lamp, preheat ballast | Mag-STD |  | 1 | 22/32 | 58 | FC22/32/1 | General
FC32/1 | Circular Fluorescent | Circular Fluorescent | FC12T9 | Fluorescent, Circline, (1) 32W lamp, preheat ballast | Mag-STD |  | 1 | 32 | 40 | FC32/1 | General
FC32/40/1 | Circular Fluorescent | Circular Fluorescent | FC32/40T9 | Fluorescent, Circlite, (1) 32W/40W lamp, preheat ballast | Mag-STD |  | 1 | 32/40 | 80 | FC32/40/1 | General
FC40/1 | Circular Fluorescent | Circular Fluorescent | FC16T9 | Fluorescent, Circline, (1) 32W lamp, preheat ballast | Mag-STD |  | 1 | 32 | 42 | FC40/1 | General
FC44/1 | Circular Fluorescent | Circular Fluorescent | FC44T9 | Fluorescent, Circlite, (1) 44W lamp, preheat ballast | Mag-STD |  | 1 | 44 | 46 | FC44/1 | General
FC6/1 | Circular Fluorescent | Circular Fluorescent | FC6T9 | Fluorescent, (1) 6" circular lamp, RS ballast | Mag-STD | 6 | 1 | 20 | 25 | FC6/1 | General
FC8/1 | Circular Fluorescent | Circular Fluorescent | FC8T9 | Fluorescent, (1) 8" circular lamp, RS ballast | Mag-STD | 8 | 1 | 22 | 26 | FC8/1 | General
FC12/2 | Circular Fluorescent | Circular Fluorescent | FC12T9 | Fluorescent, (2) 12" circular lamp, RS ballast | Mag-STD | 12 | 2 | 32 | 62 | FC12/2 | General
FC8/2 | Circular Fluorescent | Circular Fluorescent | FC8T9 | Fluorescent, (2) 8" circular lamp, RS ballast | Mag-STD | 8 | 2 | 22 | 52 | FC8/2 | General
F40EE/D1 | Delamp | Delamp | None | Fluorescent, (0) 48" lamp, Completely delamped fixture with (1) hot ballast | Mag-ES |  | 0 | 0 | 4 | F40EE/D1 | General
F40EE/D2 | Delamp | Delamp | None | Fluorescent, (0) 48" lamp, Completely delamped fixture with (2) hot ballast | Mag-ES |  | 0 | 0 | 8 | F40EE/D2 | General
ECF5/1 | Exit Sign | Exit Sign | CFT5W | EXIT Compact Fluorescent, (1) 5W lamp | Mag-STD |  | 1 | 5 | 9 | ECF5/1 | General
ECF7/1 | Exit Sign | Exit Sign | CFT7W | EXIT Compact Fluorescent, (1) 7W lamp | Mag-STD |  | 1 | 7 | 10 | ECF7/1 | General
ECF8/1 | Exit Sign | Exit Sign | F8T5 | EXIT T5 Fluorescent, (1) 8W lamp | Mag-STD |  | 1 | 8 | 12 | ECF8/1 | General
ECF9/1 | Exit Sign | Exit Sign | CFT9W | EXIT Compact Fluorescent, (1) 9W lamp | Mag-STD |  | 1 | 9 | 12 | ECF9/1 | General
EI15/1 | Exit Sign | Exit Sign | I15 | EXIT Incandescent, (1) 15W lamp |  |  | 1 | 15 | 15 | EI15/1 | General
EI20/1 | Exit Sign | Exit Sign | I20 | EXIT Incandescent, (1) 20W lamp |  |  | 1 | 20 | 20 | EI20/1 | General
EI25/1 | Exit Sign | Exit Sign | I25 | EXIT Incandescent, (1) 25W lamp |  |  | 1 | 25 | 25 | EI25/1 | General
EI34/1 | Exit Sign | Exit Sign | I34 | EXIT Incandescent, (1) 34W lamp |  |  | 1 | 34 | 34 | EI34/1 | General
EI40/1 | Exit Sign | Exit Sign | I40 | EXIT Incandescent, (1) 40W lamp |  |  | 1 | 40 | 40 | EI40/1 | General
EI5/1 | Exit Sign | Exit Sign | I5 | EXIT Incandescent, (1) 5W lamp |  |  | 1 | 5 | 5 | EI5/1 | General
EI7.5/1 | Exit Sign | Exit Sign | I7.5 | EXIT Tungsten, (1) 7.5 W lamp |  |  | 1 | 7.5 | 8 | EI7.5/1 | General
ELED0.5/1 | Exit Sign | Exit Sign | LED0.5W | EXIT Light Emitting Diode, (1) 0.5W lamp, Single Sided |  |  | 1 | 0.5 | 0.5 | ELED0.5/1 | General
ELED1.5/1 | Exit Sign | Exit Sign | LED1.5W | EXIT Light Emitting Diode, (1) 1.5W lamp, Single Sided |  |  | 1 | 1.5 | 1.5 | ELED1.5/1 | General
ELED10.5/1 | Exit Sign | Exit Sign | LED10.5W | EXIT Light Emitting Diode, (1) 10.5W lamp, Single Sided |  |  | 1 | 10.5 | 10.5 | ELED10.5/1 | General
ELED2/1 | Exit Sign | Exit Sign | LED2W | EXIT Light Emitting Diode, (1) 2W lamp, Single Sided |  |  | 1 | 2 | 2 | ELED2/1 | General
ELED3/1 | Exit Sign | Exit Sign | LED3W | EXIT Light Emitting Diode, (1) 3W lamp, Single Sided |  |  | 1 | 3 | 3 | ELED3/1 | General
ELED5/1 | Exit Sign | Exit Sign | LED5W | EXIT Light Emitting Diode, (1) 5W lamp, Single Sided |  |  | 1 | 5 | 5 | ELED5/1 | General
ELED8/1 | Exit Sign | Exit Sign | LED8W | EXIT Light Emitting Diode, (1) 8W lamp, Single Sided |  |  | 1 | 8 | 8 | ELED8/1 | General
ECF5/2 | Exit Sign | Exit Sign | CFT5W | EXIT Compact Fluorescent, (2) 5W lamp | Mag-STD |  | 2 | 5 | 20 | ECF5/2 | General
ECF7/2 | Exit Sign | Exit Sign | CFT7W | EXIT Compact Fluorescent, (2) 7W lamp | Mag-STD |  | 2 | 7 | 21 | ECF7/2 | General
ECF8/2 | Exit Sign | Exit Sign | F8T5 | EXIT T5 Fluorescent, (2) 8W lamp | Mag-STD |  | 2 | 8 | 24 | ECF8/2 | General
ECF9/2 | Exit Sign | Exit Sign | CFT9W | EXIT Compact Fluorescent, (2) 9W lamp | Mag-STD |  | 2 | 9 | 20 | ECF9/2 | General
EI10/2 | Exit Sign | Exit Sign | I10 | EXIT Incandescent, (2) 10W lamp |  |  | 2 | 10 | 20 | EI10/2 | General
EI15/2 | Exit Sign | Exit Sign | I15 | EXIT Incandescent, (2) 15W lamp |  |  | 2 | 15 | 30 | EI15/2 | General
EI20/2 | Exit Sign | Exit Sign | I20 | EXIT Incandescent, (2) 20W lamp |  |  | 2 | 20 | 40 | EI20/2 | General
EI25/2 | Exit Sign | Exit Sign | I25 | EXIT Incandescent, (2) 25W lamp |  |  | 2 | 25 | 50 | EI25/2 | General
EI34/2 | Exit Sign | Exit Sign | I34 | EXIT Incandescent, (2) 34W lamp |  |  | 2 | 34 | 68 | EI34/2 | General
EI40/2 | Exit Sign | Exit Sign | I40 | EXIT Incandescent, (2) 40W lamp |  |  | 2 | 40 | 80 | EI40/2 | General
EI5/2 | Exit Sign | Exit Sign | I5 | EXIT Incandescent, (2) 5W lamp |  |  | 2 | 5 | 10 | EI5/2 | General
EI50/2 | Exit Sign | Exit Sign | I50 | EXIT Incandescent, (2) 50W lamp |  |  | 2 | 50 | 100 | EI50/2 | General
EI7.5/2 | Exit Sign | Exit Sign | I7.5 | EXIT Tungsten, (2) 7.5 W lamp |  |  | 2 | 7.5 | 15 | EI7.5/2 | General
ELED0.5/2 | Exit Sign | Exit Sign | LED0.5W | EXIT Light Emitting Diode, (2) 0.5W lamp, Dual Sided |  |  | 2 | 0.5 | 1 | ELED0.5/2 | General
ELED1.5/2 | Exit Sign | Exit Sign | LED1.5W | EXIT Light Emitting Diode, (2) 1.5W lamp, Dual Sided |  |  | 2 | 1.5 | 3 | ELED1.5/2 | General
ELED10.5/2 | Exit Sign | Exit Sign | LED10.5W | EXIT Light Emitting Diode, (2) 10.5W lamp, Dual Sided |  |  | 2 | 10.5 | 21 | ELED10.5/2 | General
ELED2/2 | Exit Sign | Exit Sign | LED2W | EXIT Light Emitting Diode, (2) 2W lamp, Dual Sided |  |  | 2 | 2 | 4 | ELED2/2 | General
ELED3/2 | Exit Sign | Exit Sign | LED3W | EXIT Light Emitting Diode, (2) 3W lamp, Dual Sided |  |  | 2 | 3 | 6 | ELED3/2 | General
ELED5/2 | Exit Sign | Exit Sign | LED5W | EXIT Light Emitting Diode, (2) 5W lamp, Dual Sided |  |  | 2 | 5 | 10 | ELED5/2 | General
ELED8/2 | Exit Sign | Exit Sign | LED8W | EXIT Light Emitting Diode, (2) 8W lamp, Dual Sided |  |  | 2 | 8 | 16 | ELED8/2 | General
I100/1 | Incandescent | Standard Incandescent | I100 | Incandescent, (1) 100W lamp |  |  | 1 | 100 | 100 | GSL33/1 | Screw-In
I1000/1 | Incandescent | Standard Incandescent | I1000 | Incandescent, (1) 1000W lamp |  |  | 1 | 1000 | 1000 | I1000/1 | Screw-In
I100E/1 | Incandescent | Standard Incandescent | I100/ES | Incandescent, (1) 100W ES lamp |  |  | 1 | 90 | 90 | GSL28/1 | Screw-In
I100EL/1 | Incandescent | Standard Incandescent | I100/ES/LL | Incandescent, (1) 100W ES/LL lamp |  |  | 1 | 90 | 90 | GSL28/1 | Screw-In
I120/1 | Incandescent | Standard Incandescent | I120 | Incandescent, (1) 120W lamp |  |  | 1 | 120 | 120 | GSL40/1 | Screw-In
I125/1 | Incandescent | Standard Incandescent | I125 | Incandescent, (1) 125W lamp |  |  | 1 | 125 | 125 | GSL44/1 | Screw-In
I135/1 | Incandescent | Standard Incandescent | I135 | Incandescent, (1) 135W lamp |  |  | 1 | 135 | 135 | GSL48/1 | Screw-In
I15/1 | Incandescent | Standard Incandescent | I15 | Incandescent, (1) 15W lamp |  |  | 1 | 15 | 15 | I15/1 | Screw-In
I150/1 | Incandescent | Standard Incandescent | I150 | Incandescent, (1) 150W lamp |  |  | 1 | 150 | 150 | GSL58/1 | Screw-In
I1500/1 | Incandescent | Standard Incandescent | I1500 | Incandescent, (1) 1500W lamp |  |  | 1 | 1500 | 1500 | I1500/1 | Screw-In
I150E/1 | Incandescent | Standard Incandescent | I150/ES | Incandescent, (1) 150W ES lamp |  |  | 1 | 135 | 135 | GSL48/1 | Screw-In
I150EL/1 | Incandescent | Standard Incandescent | I150/ES/LL | Incandescent, (1) 150W ES/LL lamp |  |  | 1 | 135 | 135 | GSL48/1 | Screw-In
I170/1 | Incandescent | Standard Incandescent | I170 | Incandescent, (1) 170W lamp |  |  | 1 | 170 | 170 | GSL66/1 | Screw-In
I20/1 | Incandescent | Standard Incandescent | I20 | Incandescent, (1) 20W lamp |  |  | 1 | 20 | 20 | I20/1 | Screw-In
I200/1 | Incandescent | Standard Incandescent | I200 | Incandescent, (1) 200W lamp |  |  | 1 | 200 | 200 | I200/1 | Screw-In
I2000/1 | Incandescent | Standard Incandescent | I2000 | Incandescent, (1) 2000W lamp |  |  | 1 | 2000 | 2000 | I2000/1 | Screw-In
I200L/1 | Incandescent | Standard Incandescent | I200/LL | Incandescent, (1) 200W LL lamp |  |  | 1 | 200 | 200 | I200L/1 | Screw-In
I25/1 | Incandescent | Standard Incandescent | I25 | Incandescent, (1) 25W lamp |  |  | 1 | 25 | 25 | I25/1 | Screw-In
I250/1 | Incandescent | Standard Incandescent | I250 | Incandescent, (1) 250W lamp |  |  | 1 | 250 | 250 | I250/1 | Screw-In
I300/1 | Incandescent | Standard Incandescent | I300 | Incandescent, (1) 300W lamp |  |  | 1 | 300 | 300 | I300/1 | Screw-In
I34/1 | Incandescent | Standard Incandescent | I34 | Incandescent, (1) 34W lamp |  |  | 1 | 34 | 34 | GSL8/1 | Screw-In
I36/1 | Incandescent | Standard Incandescent | I36 | Incandescent, (1) 36W lamp |  |  | 1 | 36 | 36 | GSL8/1 | Screw-In
I40/1 | Incandescent | Standard Incandescent | I40 | Incandescent, (1) 40W lamp |  |  | 1 | 40 | 40 | GSL10/1 | Screw-In
I400/1 | Incandescent | Standard Incandescent | I400 | Incandescent, (1) 400W lamp |  |  | 1 | 400 | 400 | I400/1 | Screw-In
I40E/1 | Incandescent | Standard Incandescent | I40/ES | Incandescent, (1) 40W ES lamp |  |  | 1 | 34 | 34 | GSL8/1 | Screw-In
I40EL/1 | Incandescent | Standard Incandescent | I40/ES/LL | Incandescent, (1) 40W ES/LL lamp |  |  | 1 | 34 | 34 | GSL8/1 | Screw-In
I42/1 | Incandescent | Standard Incandescent | I42 | Incandescent, (1) 42W lamp |  |  | 1 | 42 | 42 | GSL11/1 | Screw-In
I448/1 | Incandescent | Standard Incandescent | I448 | Incandescent, (1) 448W lamp |  |  | 1 | 448 | 448 | I448/1 | Screw-In
I45/1 | Incandescent | Standard Incandescent | I45 | Incandescent, (1) 45W lamp |  |  | 1 | 45 | 45 | GSL11/1 | Screw-In
I50/1 | Incandescent | Standard Incandescent | I50 | Incandescent, (1) 50W lamp |  |  | 1 | 50 | 50 | GSL13/1 | Screw-In
I500/1 | Incandescent | Standard Incandescent | I500 | Incandescent, (1) 500W lamp |  |  | 1 | 500 | 500 | I500/1 | Screw-In
I52/1 | Incandescent | Standard Incandescent | I52 | Incandescent, (1) 52W lamp |  |  | 1 | 52 | 52 | GSL13/1 | Screw-In
I54/1 | Incandescent | Standard Incandescent | I54 | Incandescent, (1) 54W lamp |  |  | 1 | 54 | 54 | GSL14/1 | Screw-In
I55/1 | Incandescent | Standard Incandescent | I55 | Incandescent, (1) 55W lamp |  |  | 1 | 55 | 55 | GSL14/1 | Screw-In
I60/1 | Incandescent | Standard Incandescent | I60 | Incandescent, (1) 60W lamp |  |  | 1 | 60 | 60 | GSL17/1 | Screw-In
I60E/1 | Incandescent | Standard Incandescent | I60/ES | Incandescent, (1) 60W ES lamp |  |  | 1 | 52 | 52 | GSL13/1 | Screw-In
I60EL/1 | Incandescent | Standard Incandescent | I60/ES/LL | Incandescent, (1) 60W ES/LL lamp |  |  | 1 | 52 | 52 | GSL13/1 | Screw-In
I65/1 | Incandescent | Standard Incandescent | I65 | Incandescent, (1) 65W lamp |  |  | 1 | 65 | 65 | GSL18/1 | Screw-In
I67/1 | Incandescent | Standard Incandescent | I67 | Incandescent, (1) 67W lamp |  |  | 1 | 67 | 67 | GSL19/1 | Screw-In
I69/1 | Incandescent | Standard Incandescent | I69 | Incandescent, (1) 69W lamp |  |  | 1 | 69 | 69 | GSL19/1 | Screw-In
I7.5/1 | Incandescent | Standard Incandescent | I7.5 | Tungsten exit light, (1) 7.5 W lamp, used in night light application |  |  | 1 | 7.5 | 8 | I7.5/1 | Screw-In
I72/1 | Incandescent | Standard Incandescent | I72 | Incandescent, (1) 72W lamp |  |  | 1 | 72 | 72 | GSL20/1 | Screw-In
I75/1 | Incandescent | Standard Incandescent | I75 | Incandescent, (1) 75W lamp |  |  | 1 | 75 | 75 | GSL23/1 | Screw-In
I750/1 | Incandescent | Standard Incandescent | I750 | Incandescent, (1) 750W lamp |  |  | 1 | 750 | 750 | I750/1 | Screw-In
I75E/1 | Incandescent | Standard Incandescent | I75/ES | Incandescent, (1) 75W ES lamp |  |  | 1 | 67 | 67 | GSL19/1 | Screw-In
I75EL/1 | Incandescent | Standard Incandescent | I75/ES/LL | Incandescent, (1) 75W ES/LL lamp |  |  | 1 | 67 | 67 | GSL19/1 | Screw-In
I80/1 | Incandescent | Standard Incandescent | I80 | Incandescent, (1) 80W lamp |  |  | 1 | 80 | 80 | GSL25/1 | Screw-In
I85/1 | Incandescent | Standard Incandescent | I85 | Incandescent, (1) 85W lamp |  |  | 1 | 85 | 85 | GSL26/1 | Screw-In
I90/1 | Incandescent | Standard Incandescent | I90 | Incandescent, (1) 90W lamp |  |  | 1 | 90 | 90 | GSL28/1 | Screw-In
I93/1 | Incandescent | Standard Incandescent | I93 | Incandescent, (1) 93W lamp |  |  | 1 | 93 | 93 | GSL29/1 | Screw-In
I95/1 | Incandescent | Standard Incandescent | I95 | Incandescent, (1) 95W lamp |  |  | 1 | 95 | 95 | GSL30/1 | Screw-In
I100/2 | Incandescent | Standard Incandescent | I100 | Incandescent, (2) 100W lamp |  |  | 2 | 100 | 200 | GSL33/2 | Screw-In
I120/2 | Incandescent | Standard Incandescent | I120 | Incandescent, (2) 120W lamp |  |  | 2 | 120 | 240 | GSL40/2 | Screw-In
I135/2 | Incandescent | Standard Incandescent | I135 | Incandescent, (2) 135W lamp |  |  | 2 | 135 | 270 | GSL48/2 | Screw-In
I15/2 | Incandescent | Standard Incandescent | I15 | Incandescent, (2) 15W lamp |  |  | 2 | 15 | 30 | I15/2 | Screw-In
I150/2 | Incandescent | Standard Incandescent | I150 | Incandescent, (2) 150W lamp |  |  | 2 | 150 | 300 | GSL58/2 | Screw-In
I20/2 | Incandescent | Standard Incandescent | I20 | Incandescent, (2) 20W lamp |  |  | 2 | 20 | 40 | I20/2 | Screw-In
I200/2 | Incandescent | Standard Incandescent | I200 | Incandescent, (2) 200W lamp |  |  | 2 | 200 | 400 | I200/2 | Screw-In
I25/2 | Incandescent | Standard Incandescent | I25 | Incandescent, (2) 25W lamp |  |  | 2 | 25 | 50 | I25/2 | Screw-In
I34/2 | Incandescent | Standard Incandescent | I34 | Incandescent, (2) 34W lamp |  |  | 2 | 34 | 68 | GSL8/2 | Screw-In
I40/2 | Incandescent | Standard Incandescent | I40 | Incandescent, (2) 40W lamp |  |  | 2 | 40 | 80 | GSL10/2 | Screw-In
I50/2 | Incandescent | Standard Incandescent | I50 | Incandescent, (2) 50W lamp |  |  | 2 | 50 | 100 | GSL13/2 | Screw-In
I52/2 | Incandescent | Standard Incandescent | I52 | Incandescent, (2) 52W lamp |  |  | 2 | 52 | 104 | GSL13/2 | Screw-In
I54/2 | Incandescent | Standard Incandescent | I54 | Incandescent, (2) 54W lamp |  |  | 2 | 54 | 108 | GSL14/2 | Screw-In
I55/2 | Incandescent | Standard Incandescent | I55 | Incandescent, (2) 55W lamp |  |  | 2 | 55 | 110 | GSL14/2 | Screw-In
I60/2 | Incandescent | Standard Incandescent | I60 | Incandescent, (2) 60W lamp |  |  | 2 | 60 | 120 | GSL17/2 | Screw-In
I65/2 | Incandescent | Standard Incandescent | I65 | Incandescent, (2) 65W lamp |  |  | 2 | 65 | 130 | GSL18/2 | Screw-In
I67/2 | Incandescent | Standard Incandescent | I67 | Incandescent, (2) 67W lamp |  |  | 2 | 67 | 134 | GSL19/2 | Screw-In
I7.5/2 | Incandescent | Standard Incandescent | I7.5 | Tungsten exit light, (2) 7.5 W lamp, used in night light application |  |  | 2 | 7.5 | 15 | I7.5/2 | Screw-In
I75/2 | Incandescent | Standard Incandescent | I75 | Incandescent, (2) 75W lamp |  |  | 2 | 75 | 150 | GSL23/2 | Screw-In
I90/2 | Incandescent | Standard Incandescent | I90 | Incandescent, (2) 90W lamp |  |  | 2 | 90 | 180 | GSL28/2 | Screw-In
I95/2 | Incandescent | Standard Incandescent | I95 | Incandescent, (2) 95W lamp |  |  | 2 | 95 | 190 | GSL30/2 | Screw-In
I100/3 | Incandescent | Standard Incandescent | I100 | Incandescent, (3) 100W lamp |  |  | 3 | 100 | 300 | GSL33/3 | Screw-In
I60/3 | Incandescent | Standard Incandescent | I60 | Incandescent, (3) 60W lamp |  |  | 3 | 60 | 180 | GSL17/3 | Screw-In
I67/3 | Incandescent | Standard Incandescent | I67 | Incandescent, (3) 67W lamp |  |  | 3 | 67 | 201 | GSL19/3 | Screw-In
I75/3 | Incandescent | Standard Incandescent | I75 | Incandescent, (3) 75W lamp |  |  | 3 | 75 | 225 | GSL23/3 | Screw-In
I90/3 | Incandescent | Standard Incandescent | I90 | Incandescent, (3) 90W lamp |  |  | 3 | 90 | 270 | GSL28/3 | Screw-In
I100/4 | Incandescent | Standard Incandescent | I100 | Incandescent, (4) 100W lamp |  |  | 4 | 100 | 400 | GSL33/4 | Screw-In
I25/4 | Incandescent | Standard Incandescent | I25 | Incandescent, (4) 25W lamp |  |  | 4 | 25 | 100 | I25/4 | Screw-In
I60/4 | Incandescent | Standard Incandescent | I60 | Incandescent, (4) 60W lamp |  |  | 4 | 60 | 240 | GSL17/4 | Screw-In
I75/4 | Incandescent | Standard Incandescent | I75 | Incandescent, (4) 75W lamp |  |  | 4 | 75 | 300 | GSL23/4 | Screw-In
I100/5 | Incandescent | Standard Incandescent | I100 | Incandescent, (5) 100W lamp |  |  | 5 | 100 | 500 | GSL33/5 | Screw-In
I60/5 | Incandescent | Standard Incandescent | I60 | Incandescent, (5) 60W lamp |  |  | 5 | 60 | 300 | GSL17/5 | Screw-In
H100/1 | Incandescent | Halogen Incandescent | H100 | Halogen Incandescent, (1) 100W lamp |  |  | 1 | 100 | 100 | GSL46/1 | Screw-In
H1000/1 | Incandescent | Halogen Incandescent | H1000 | Halogen Incandescent, (1) 1000W lamp |  |  | 1 | 1000 | 1000 | H1000/1 | Screw-In
H1200/1 | Incandescent | Halogen Incandescent | H1200 | Halogen Incandescent, (1) 1200W lamp |  |  | 1 | 1200 | 1200 | H1200/1 | Screw-In
H150/1 | Incandescent | Halogen Incandescent | H150 | Halogen Incandescent, (1) 150W lamp |  |  | 1 | 150 | 150 | GSL69/1 | Screw-In
H1500/1 | Incandescent | Halogen Incandescent | H1500 | Halogen Incandescent, (1) 1500W lamp |  |  | 1 | 1500 | 1500 | H1500/1 | Screw-In
H200/1 | Incandescent | Halogen Incandescent | H200 | Halogen Incandescent, (1) 200W lamp |  |  | 1 | 200 | 200 | H200/1 | Screw-In
H250/1 | Incandescent | Halogen Incandescent | H250 | Halogen Incandescent, (1) 250W lamp |  |  | 1 | 250 | 250 | H250/1 | Screw-In
H300/1 | Incandescent | Halogen Incandescent | H300 | Halogen Incandescent, (1) 300W lamp |  |  | 1 | 300 | 300 | H300/1 | Screw-In
H35/1 | Incandescent | Halogen Incandescent | H35 | Halogen Incandescent, (1) 35W lamp |  |  | 1 | 35 | 35 | GSL12/1 | Screw-In
H350/1 | Incandescent | Halogen Incandescent | H350 | Halogen Incandescent, (1) 350W lamp |  |  | 1 | 350 | 350 | H350/1 | Screw-In
H40/1 | Incandescent | Halogen Incandescent | H40 | Halogen Incandescent, (1) 40W lamp |  |  | 1 | 40 | 40 | GSL14/1 | Screw-In
H400/1 | Incandescent | Halogen Incandescent | H400 | Halogen Incandescent, (1) 400W lamp |  |  | 1 | 400 | 400 | H400/1 | Screw-In
H42/1 | Incandescent | Halogen Incandescent | H42 | Halogen Incandescent, (1) 42W lamp |  |  | 1 | 42 | 42 | GSL14/1 | Screw-In
H425/1 | Incandescent | Halogen Incandescent | H425 | Halogen Incandescent, (1) 425W lamp |  |  | 1 | 425 | 425 | H425/1 | Screw-In
H45/1 | Incandescent | Halogen Incandescent | H45 | Halogen Incandescent, (1) 45W lamp |  |  | 1 | 45 | 45 | GSL17/1 | Screw-In
H50/1 | Incandescent | Halogen Incandescent | H50 | Halogen Incandescent, (1) 50W lamp |  |  | 1 | 50 | 50 | GSL19/1 | Screw-In
H500/1 | Incandescent | Halogen Incandescent | H500 | Halogen Incandescent, (1) 500W lamp |  |  | 1 | 500 | 500 | H500/1 | Screw-In
H52/1 | Incandescent | Halogen Incandescent | H52 | Halogen Incandescent, (1) 52W lamp |  |  | 1 | 52 | 52 | GSL20/1 | Screw-In
H55/1 | Incandescent | Halogen Incandescent | H55 | Halogen Incandescent, (1) 55W lamp |  |  | 1 | 55 | 55 | GSL24/1 | Screw-In
H60/1 | Incandescent | Halogen Incandescent | H60 | Halogen Incandescent, (1) 60W lamp |  |  | 1 | 60 | 60 | GSL26/1 | Screw-In
H72/1 | Incandescent | Halogen Incandescent | H72 | Halogen Incandescent, (1) 72W lamp |  |  | 1 | 72 | 72 | GSL33/1 | Screw-In
H75/1 | Incandescent | Halogen Incandescent | H75 | Halogen Incandescent, (1) 75W lamp |  |  | 1 | 75 | 75 | GSL34/1 | Screw-In
H750/1 | Incandescent | Halogen Incandescent | H750 | Halogen Incandescent, (1) 750W lamp |  |  | 1 | 750 | 750 | H750/1 | Screw-In
H90/1 | Incandescent | Halogen Incandescent | H90 | Halogen Incandescent, (1) 90W lamp |  |  | 1 | 90 | 90 | GSL41/1 | Screw-In
H900/1 | Incandescent | Halogen Incandescent | H900 | Halogen Incandescent, (1) 900W lamp |  |  | 1 | 900 | 900 | H900/1 | Screw-In
HLV20/1 | Incandescent | Halogen Incandescent | H20/LV | Halogen Low Voltage Incandescent, (1) 20W lamp |  |  | 1 | 20 | 30 | HLV20/1 | Screw-In
HLV25/1 | Incandescent | Halogen Incandescent | H25/LV | Halogen Low Voltage Incandescent, (1) 25W lamp |  |  | 1 | 25 | 35 | GSL9/1 | Screw-In
HLV35/1 | Incandescent | Halogen Incandescent | H35/LV | Halogen Low Voltage Incandescent, (1) 35W lamp |  |  | 1 | 35 | 45 | GSL12/1 | Screw-In
HLV42/1 | Incandescent | Halogen Incandescent | H42/LV | Halogen Low Voltage Incandescent, (1) 42W lamp |  |  | 1 | 42 | 52 | GSL14/1 | Screw-In
HLV50/1 | Incandescent | Halogen Incandescent | H50/LV | Halogen Low Voltage Incandescent, (1) 50W lamp |  |  | 1 | 50 | 60 | GSL19/1 | Screw-In
HLV65/1 | Incandescent | Halogen Incandescent | H65/LV | Halogen Low Voltage Incandescent, (1) 65W lamp |  |  | 1 | 65 | 75 | GSL29/1 | Screw-In
HLV75/1 | Incandescent | Halogen Incandescent | H75/LV | Halogen Low Voltage Incandescent, (1) 75W lamp |  |  | 1 | 75 | 85 | GSL34/1 | Screw-In
H150/2 | Incandescent | Halogen Incandescent | H150 | Halogen Incandescent, (2) 150W lamp |  |  | 2 | 150 | 300 | GSL69/2 | Screw-In
H45/2 | Incandescent | Halogen Incandescent | H45 | Halogen Incandescent, (2) 45W lamp |  |  | 2 | 45 | 90 | GSL17/2 | Screw-In
H50/2 | Incandescent | Halogen Incandescent | H50 | Halogen Incandescent, (2) 50W lamp |  |  | 2 | 50 | 100 | GSL19/2 | Screw-In
H55/2 | Incandescent | Halogen Incandescent | H55 | Halogen Incandescent, (2) 55W lamp |  |  | 2 | 55 | 110 | GSL24/2 | Screw-In
H75/2 | Incandescent | Halogen Incandescent | H75 | Halogen Incandescent, (2) 75W lamp |  |  | 2 | 75 | 150 | GSL34/2 | Screw-In
H90/2 | Incandescent | Halogen Incandescent | H90 | Halogen Incandescent, (2) 90W lamp |  |  | 2 | 90 | 180 | GSL41/2 | Screw-In
QL55/1 | Induction Fluorescent | Induction Fluorescent | QL55 | QL Induction, (1) 55W lamp | Generator |  | 1 | 55 | 55 | QL55/1 | Screw-In
QL85/1 | Induction Fluorescent | Induction Fluorescent | QL85 | QL Induction, (1) 85W lamp | Generator |  | 1 | 85 | 85 | QL85/1 | Screw-In
QL165/1 | Induction Fluorescent | Induction Fluorescent | QL165 | QL Induction, (1) 165W lamp | Generator |  | 1 | 165 | 165 | QL165/1 | Screw-In
MH100/1 | High Intensity Discharge | Metal Halide | MH100 | Metal Halide, (1) 100W lamp | CWA |  | 1 | 100 | 128 | MH100/1 | General
MH1000/1 | High Intensity Discharge | Metal Halide | MH1000 | Metal Halide, (1) 1000W lamp | CWA |  | 1 | 1000 | 1080 | MH1000/1 | General
MH150/1 | High Intensity Discharge | Metal Halide | MH150 | Metal Halide, (1) 150W lamp | CWA |  | 1 | 150 | 190 | MH150/1 | General
MH1500/1 | High Intensity Discharge | Metal Halide | MH1500 | Metal Halide, (1) 1500W lamp | CWA |  | 1 | 1500 | 1610 | MH1500/1 | General
MH175/1 | High Intensity Discharge | Metal Halide | MH175 | Metal Halide, (1) 175W lamp | CWA |  | 1 | 175 | 215 | MH175/1 | General
MH1800/1 | High Intensity Discharge | Metal Halide | MH1800 | Metal Halide, (1) 1800W lamp | CWA |  | 1 | 1800 | 1875 | MH1800/1 | General
MH200/1 | High Intensity Discharge | Metal Halide | MH200 | Metal Halide, (1) 200W lamp | CWA |  | 1 | 200 | 232 | MH200/1 | General
MH250/1 | High Intensity Discharge | Metal Halide | MH250 | Metal Halide, (1) 250W lamp | CWA |  | 1 | 250 | 295 | MH250/1 | General
MH32/1 | High Intensity Discharge | Metal Halide | MH32 | Metal Halide, (1) 32W lamp | CWA |  | 1 | 32 | 43 | MH32/1 | General
MH300/1 | High Intensity Discharge | Metal Halide | MH300 | Metal Halide, (1) 300W lamp | CWA |  | 1 | 300 | 342 | MH300/1 | General
MH320/1 | High Intensity Discharge | Metal Halide | MH320 | Metal Halide, (1) 320W lamp | CWA |  | 1 | 320 | 365 | MH320/1 | General
MH350/1 | High Intensity Discharge | Metal Halide | MH350 | Metal Halide, (1) 350W lamp | CWA |  | 1 | 350 | 400 | MH350/1 | General
MH360/1 | High Intensity Discharge | Metal Halide | MH360 | Metal Halide, (1) 360W lamp | CWA |  | 1 | 360 | 430 | MH360/1 | General
MH400/1 | High Intensity Discharge | Metal Halide | MH400 | Metal Halide, (1) 400W lamp | CWA |  | 1 | 400 | 458 | MH400/1 | General
MH450/1 | High Intensity Discharge | Metal Halide | MH450 | Metal Halide, (1) 450W lamp | CWA |  | 1 | 450 | 508 | MH450/1 | General
MH35/1 | High Intensity Discharge | Metal Halide | MH35 | Metal Halide, (1) 35W lamp | CWA |  | 1 | 35 | 44 | MH35/1 | General
MH50/1 | High Intensity Discharge | Metal Halide | MH50 | Metal Halide, (1) 50W lamp | CWA |  | 1 | 50 | 72 | MH50/1 | General
MH70/1 | High Intensity Discharge | Metal Halide | MH70 | Metal Halide, (1) 70W lamp | CWA |  | 1 | 70 | 95 | MH70/1 | General
MH750/1 | High Intensity Discharge | Metal Halide | MH750 | Metal Halide, (1) 750W lamp | CWA |  | 1 | 750 | 850 | MH750/1 | General
MH400/2 | High Intensity Discharge | Metal Halide | MH400 | Metal Halide, (2) 400W lamp | CWA |  | 2 | 400 | 916 | MH400/2 | General
MHPS/LR/100/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS100 | Metal Halide Pulse Start, (1) 100W lamp w/ Linear Reactor Ballast | LR |  | 1 | 100 | 118 | MHPS/LR/100/1 | General
MHPS/LR/150/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS150 | Metal Halide Pulse Start, (1) 150W lamp w/ Linear Reactor Ballast | LR |  | 1 | 150 | 170 | MHPS/LR/150/1 | General
MHPS/LR/175/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS175 | Metal Halide Pulse Start, (1) 175W lamp w/ Linear Reactor Ballast | LR |  | 1 | 175 | 194 | MHPS/LR/175/1 | General
MHPS/LR/200/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS200 | Metal Halide Pulse Start, (1) 200W lamp w/ Linear Reactor Ballast | LR |  | 1 | 200 | 219 | MHPS/LR/200/1 | General
MHPS/LR/250/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS250 | Metal Halide Pulse Start, (1) 250W lamp w/ Linear Reactor Ballast | LR |  | 1 | 250 | 275 | MHPS/LR/250/1 | General
MHPS/LR/300/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS300 | Metal Halide Pulse Start, (1) 300W lamp w/ Linear Reactor Ballast | LR |  | 1 | 300 | 324 | MHPS/LR/300/1 | General
MHPS/LR/320/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS320 | Metal Halide Pulse Start, (1) 320W lamp w/ Linear Reactor Ballast | LR |  | 1 | 320 | 349 | MHPS/LR/320/1 | General
MHPS/LR/350/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS350 | Metal Halide Pulse Start, (1) 350W lamp w/ Linear Reactor Ballast | LR |  | 1 | 350 | 380 | MHPS/LR/350/1 | General
MHPS/LR/400/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS400 | Metal Halide Pulse Start, (1) 400W lamp w/ Linear Reactor Ballast | LR |  | 1 | 400 | 435 | MHPS/LR/400/1 | General
MHPS/LR/450/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS450 | Metal Halide Pulse Start, (1) 450W lamp w/ Linear Reactor Ballast | LR |  | 1 | 450 | 485 | MHPS/LR/450/1 | General
MHPS/LR/750/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS750 | Metal Halide Pulse Start, (1) 750W lamp w/ Linear Reactor Ballast | LR |  | 1 | 750 | 805 | MHPS/LR/750/1 | General
MHPS/SCWA/100/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS100 | Metal Halide Pulse Start, (1) 100W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA |  | 1 | 100 | 128 | MHPS/SCWA/100/1 | General
MHPS/SCWA/1000/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS1000 | Metal Halide Pulse Start, (1) 1000W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA |  | 1 | 1000 | 1080 | MHPS/SCWA/1000/1 | General
MHPS/SCWA/150/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS150 | Metal Halide Pulse Start, (1) 150W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA |  | 1 | 150 | 190 | MHPS/SCWA/150/1 | General
MHPS/SCWA/175/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS175 | Metal Halide Pulse Start, (1) 175W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA |  | 1 | 175 | 208 | MHPS/SCWA/175/1 | General
MHPS/SCWA/200/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS200 | Metal Halide Pulse Start, (1) 200W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA |  | 1 | 200 | 232 | MHPS/SCWA/200/1 | General
MHPS/SCWA/250/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS250 | Metal Halide Pulse Start, (1) 250W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA |  | 1 | 250 | 288 | MHPS/SCWA/250/1 | General
MHPS/SCWA/300/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS300 | Metal Halide Pulse Start, (1) 300W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA |  | 1 | 300 | 342 | MHPS/SCWA/300/1 | General
MHPS/SCWA/320/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS320 | Metal Halide Pulse Start, (1) 320W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA |  | 1 | 320 | 368 | MHPS/SCWA/320/1 | General
MHPS/SCWA/350/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS350 | Metal Halide Pulse Start, (1) 350W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA |  | 1 | 350 | 400 | MHPS/SCWA/350/1 | General
MHPS/SCWA/400/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS400 | Metal Halide Pulse Start, (1) 400W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA |  | 1 | 400 | 450 | MHPS/SCWA/400/1 | General
MHPS/SCWA/450/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS450 | Metal Halide Pulse Start, (1) 450W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA |  | 1 | 450 | 506 | MHPS/SCWA/450/1 | General
MHPS/SCWA/750/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS750 | Metal Halide Pulse Start, (1) 750W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA |  | 1 | 750 | 815 | MHPS/SCWA/750/1 | General
HPS100/1 | High Intensity Discharge | High Pressure Sodium | HPS100 | High Pressure Sodium, (1) 100W lamp | CWA |  | 1 | 100 | 138 | HPS100/1 | General
HPS1000/1 | High Intensity Discharge | High Pressure Sodium | HPS1000 | High Pressure Sodium, (1) 1000W lamp | CWA |  | 1 | 1000 | 1100 | HPS1000/1 | General
HPS150/1 | High Intensity Discharge | High Pressure Sodium | HPS150 | High Pressure Sodium, (1) 150W lamp | CWA |  | 1 | 150 | 188 | HPS150/1 | General
HPS200/1 | High Intensity Discharge | High Pressure Sodium | HPS200 | High Pressure Sodium, (1) 200W lamp | CWA |  | 1 | 200 | 250 | HPS200/1 | General
HPS225/1 | High Intensity Discharge | High Pressure Sodium | HPS225 | High Pressure Sodium, (1) 225W lamp | CWA |  | 1 | 225 | 275 | HPS225/1 | General
HPS250/1 | High Intensity Discharge | High Pressure Sodium | HPS250 | High Pressure Sodium, (1) 250W lamp | CWA |  | 1 | 250 | 295 | HPS250/1 | General
HPS310/1 | High Intensity Discharge | High Pressure Sodium | HPS310 | High Pressure Sodium, (1) 310W lamp | CWA |  | 1 | 310 | 365 | HPS310/1 | General
HPS35/1 | High Intensity Discharge | High Pressure Sodium | HPS35 | High Pressure Sodium, (1) 35W lamp | CWA |  | 1 | 35 | 46 | HPS35/1 | General
HPS360/1 | High Intensity Discharge | High Pressure Sodium | HPS360 | High Pressure Sodium, (1) 360W lamp | CWA |  | 1 | 360 | 414 | HPS360/1 | General
HPS400/1 | High Intensity Discharge | High Pressure Sodium | HPS400 | High Pressure Sodium, (1) 400W lamp | CWA |  | 1 | 400 | 465 | HPS400/1 | General
HPS50/1 | High Intensity Discharge | High Pressure Sodium | HPS50 | High Pressure Sodium, (1) 50W lamp | CWA |  | 1 | 50 | 66 | HPS50/1 | General
HPS600/1 | High Intensity Discharge | High Pressure Sodium | HPS600 | High Pressure Sodium, (1) 600W lamp | CWA |  | 1 | 600 | 675 | HPS600/1 | General
HPS70/1 | High Intensity Discharge | High Pressure Sodium | HPS70 | High Pressure Sodium, (1) 70W lamp | CWA |  | 1 | 70 | 95 | HPS70/1 | General
HPS750/1 | High Intensity Discharge | High Pressure Sodium | HPS750 | High Pressure Sodium, (1) 750W lamp | CWA |  | 1 | 750 | 835 | HPS750/1 | General
MV100/1 | High Intensity Discharge | Mercury Vapor | MV100 | Mercury Vapor, (1) 100W lamp | CWA |  | 1 | 100 | 125 | MV100/1 | General
MV1000/1 | High Intensity Discharge | Mercury Vapor | MV1000 | Mercury Vapor, (1) 1000W lamp | CWA |  | 1 | 1000 | 1075 | MV1000/1 | General
MV175/1 | High Intensity Discharge | Mercury Vapor | MV175 | Mercury Vapor, (1) 175W lamp | CWA |  | 1 | 175 | 205 | MV175/1 | General
MV250/1 | High Intensity Discharge | Mercury Vapor | MV250 | Mercury Vapor, (1) 250W lamp | CWA |  | 1 | 250 | 290 | MV250/1 | General
MV40/1 | High Intensity Discharge | Mercury Vapor | MV40 | Mercury Vapor, (1) 40W lamp | CWA |  | 1 | 40 | 50 | MV40/1 | General
MV400/1 | High Intensity Discharge | Mercury Vapor | MV400 | Mercury Vapor, (1) 400W lamp | CWA |  | 1 | 400 | 455 | MV400/1 | General
MV50/1 | High Intensity Discharge | Mercury Vapor | MV50 | Mercury Vapor, (1) 50W lamp | CWA |  | 1 | 50 | 74 | MV50/1 | General
MV700/1 | High Intensity Discharge | Mercury Vapor | MV700 | Mercury Vapor, (1) 700W lamp | CWA |  | 1 | 700 | 780 | MV700/1 | General
MV75/1 | High Intensity Discharge | Mercury Vapor | MV75 | Mercury Vapor, (1) 75W lamp | CWA |  | 1 | 75 | 93 | MV75/1 | General
MV400/2 | High Intensity Discharge | Mercury Vapor | MV400 | Mercury Vapor, (2) 400W lamp | CWA |  | 2 | 400 | 910 | MV400/2 | General
Cut Sheet 1 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 1 | Edit
Cut Sheet 2 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 2 | Edit
Cut Sheet 3 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 3 | Edit
Cut Sheet 4 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 4 | Edit
Cut Sheet 5 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 5 | Edit
Cut Sheet 6 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 6 | Edit
Cut Sheet 7 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 7 | Edit
Cut Sheet 8 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 8 | Edit
Cut Sheet 9 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 9 | Edit
Cut Sheet 10 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 10 | Edit
Cut Sheet 11 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 11 | Edit
Cut Sheet 12 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 12 | Edit
Cut Sheet 13 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 13 | Edit
Cut Sheet 14 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 14 | Edit
Cut Sheet 15 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 15 | Edit
Cut Sheet 16 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 16 | Edit
Cut Sheet 17 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 17 | Edit
Cut Sheet 18 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 18 | Edit
Cut Sheet 19 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 19 | Edit
Cut Sheet 20 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 20 | Edit
Cut Sheet 21 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 21 | Edit
Cut Sheet 22 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 22 | Edit
Cut Sheet 23 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 23 | Edit
Cut Sheet 24 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 24 | Edit
Cut Sheet 25 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 25 | Edit
Cut Sheet 26 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 26 | Edit
Cut Sheet 27 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 27 | Edit
Cut Sheet 28 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 28 | Edit
Cut Sheet 29 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 29 | Edit
Cut Sheet 30 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 30 | Edit
Cut Sheet 31 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 31 | Edit
Cut Sheet 32 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 32 | Edit
Cut Sheet 33 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 33 | Edit
Cut Sheet 34 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 34 | Edit
Cut Sheet 35 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 35 | Edit
Cut Sheet 36 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 36 | Edit
Cut Sheet 37 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 37 | Edit
Cut Sheet 38 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 38 | Edit
Cut Sheet 39 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 39 | Edit
Cut Sheet 40 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 40 | Edit
Cut Sheet 41 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 41 | Edit
Cut Sheet 42 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 42 | Edit
Cut Sheet 43 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 43 | Edit
Cut Sheet 44 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 44 | Edit
Cut Sheet 45 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 45 | Edit
Cut Sheet 46 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 46 | Edit
Cut Sheet 47 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 47 | Edit
Cut Sheet 48 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 48 | Edit
Cut Sheet 49 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 49 | Edit
Cut Sheet 50 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit | Cut Sheet 50 | Edit
F26ILL | T12 EPACT/EISA Baseline | EPACT/EISA Compliance | N/A | Baseline Code for 24" 6-Lamp T12 EPACT/EISA Compliant T8 | N/A | 24 | 6 | 17 | 87 | N/A | General
F36ILL | T12 EPACT/EISA Baseline | EPACT/EISA Compliance | N/A | Baseline Code for 36" 6-Lamp T12 EPACT/EISA Compliant T8 | N/A | 36 | 6 | 25 | 128 | N/A | General
F61ILL | T12 EPACT/EISA Baseline | EPACT/EISA Compliance | N/A | Baseline Code for 72" 1-Lamp T12 EPACT/EISA Compliant T8 | N/A | 72 | 1 | 65 | 55 | N/A | General
F62ILL | T12 EPACT/EISA Baseline | EPACT/EISA Compliance | N/A | Baseline Code for 72" 2-Lamp T12 EPACT/EISA Compliant T8 | N/A | 72 | 2 | 65 | 111 | N/A | General
F63ILL | T12 EPACT/EISA Baseline | EPACT/EISA Compliance | N/A | Baseline Code for 72" 3-Lamp T12 EPACT/EISA Compliant T8 | N/A | 72 | 3 | 65 | 166 | N/A | General
F64ILL | T12 EPACT/EISA Baseline | EPACT/EISA Compliance | N/A | Baseline Code for 72" 4-Lamp T12 EPACT/EISA Compliant T8 | N/A | 72 | 4 | 65 | 221 | N/A | General
F83LHL | T12 EPACT/EISA Baseline | EPACT/EISA Compliance | N/A | Baseline Code for 96" 3-Lamp T12HO EPACT/EISA Compliant T8 | N/A | 96 | 3 | 86 | 253 | N/A | General
F86LHL | T12 EPACT/EISA Baseline | EPACT/EISA Compliance | N/A | Baseline Code for 96" 6-Lamp T12HO EPACT/EISA Compliant T8 | N/A | 96 | 6 | 86 | 506 | N/A | General
GSL33/1 | GSL | GFL Screw-In | GSL33 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 33W lamp | N/A |  | 1 | 33 | 33 | N/A | Screw-In
GSL28/1 | GSL | GFL Screw-In | GSL28 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 28W lamp | N/A |  | 1 | 28 | 28 | N/A | Screw-In
GSL40/1 | GSL | GFL Screw-In | GSL40 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 40W lamp | N/A |  | 1 | 40 | 40 | N/A | Screw-In
GSL44/1 | GSL | GFL Screw-In | GSL44 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 44W lamp | N/A |  | 1 | 44 | 44 | N/A | Screw-In
GSL48/1 | GSL | GFL Screw-In | GSL48 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 48W lamp | N/A |  | 1 | 48 | 48 | N/A | Screw-In
GSL58/1 | GSL | GFL Screw-In | GSL58 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 58W lamp | N/A |  | 1 | 58 | 58 | N/A | Screw-In
GSL66/1 | GSL | GFL Screw-In | GSL66 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 66W lamp | N/A |  | 1 | 66 | 66 | N/A | Screw-In
GSL8/1 | GSL | GFL Screw-In | GSL8 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 8W lamp | N/A |  | 1 | 8 | 8 | N/A | Screw-In
GSL10/1 | GSL | GFL Screw-In | GSL10 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 10W lamp | N/A |  | 1 | 10 | 10 | N/A | Screw-In
GSL11/1 | GSL | GFL Screw-In | GSL11 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 11W lamp | N/A |  | 1 | 11 | 11 | N/A | Screw-In
GSL13/1 | GSL | GFL Screw-In | GSL13 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 13W lamp | N/A |  | 1 | 13 | 13 | N/A | Screw-In
GSL14/1 | GSL | GFL Screw-In | GSL14 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 14W lamp | N/A |  | 1 | 14 | 14 | N/A | Screw-In
GSL17/1 | GSL | GFL Screw-In | GSL17 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 17W lamp | N/A |  | 1 | 17 | 17 | N/A | Screw-In
GSL18/1 | GSL | GFL Screw-In | GSL18 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 18W lamp | N/A |  | 1 | 18 | 18 | N/A | Screw-In
GSL19/1 | GSL | GFL Screw-In | GSL19 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 19W lamp | N/A |  | 1 | 19 | 19 | N/A | Screw-In
GSL20/1 | GSL | GFL Screw-In | GSL20 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 20W lamp | N/A |  | 1 | 20 | 20 | N/A | Screw-In
GSL23/1 | GSL | GFL Screw-In | GSL23 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 23W lamp | N/A |  | 1 | 23 | 23 | N/A | Screw-In
GSL25/1 | GSL | GFL Screw-In | GSL25 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 25W lamp | N/A |  | 1 | 25 | 25 | N/A | Screw-In
GSL26/1 | GSL | GFL Screw-In | GSL26 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 26W lamp | N/A |  | 1 | 26 | 26 | N/A | Screw-In
GSL29/1 | GSL | GFL Screw-In | GSL29 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 29W lamp | N/A |  | 1 | 29 | 29 | N/A | Screw-In
GSL30/1 | GSL | GFL Screw-In | GSL30 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 30W lamp | N/A |  | 1 | 30 | 30 | N/A | Screw-In
GSL33/2 | GSL | GFL Screw-In | GSL33 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 33W lamp | N/A |  | 2 | 33 | 66 | N/A | Screw-In
GSL40/2 | GSL | GFL Screw-In | GSL40 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 40W lamp | N/A |  | 2 | 40 | 80 | N/A | Screw-In
GSL48/2 | GSL | GFL Screw-In | GSL48 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 48W lamp | N/A |  | 2 | 48 | 96 | N/A | Screw-In
GSL58/2 | GSL | GFL Screw-In | GSL58 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 58W lamp | N/A |  | 2 | 58 | 116 | N/A | Screw-In
GSL8/2 | GSL | GFL Screw-In | GSL8 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 8W lamp | N/A |  | 2 | 8 | 16 | N/A | Screw-In
GSL10/2 | GSL | GFL Screw-In | GSL10 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 10W lamp | N/A |  | 2 | 10 | 20 | N/A | Screw-In
GSL13/2 | GSL | GFL Screw-In | GSL13 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 13W lamp | N/A |  | 2 | 13 | 26 | N/A | Screw-In
GSL14/2 | GSL | GFL Screw-In | GSL14 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 14W lamp | N/A |  | 2 | 14 | 28 | N/A | Screw-In
GSL17/2 | GSL | GFL Screw-In | GSL17 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 17W lamp | N/A |  | 2 | 17 | 34 | N/A | Screw-In
GSL18/2 | GSL | GFL Screw-In | GSL18 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 18W lamp | N/A |  | 2 | 18 | 36 | N/A | Screw-In
GSL19/2 | GSL | GFL Screw-In | GSL19 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 19W lamp | N/A |  | 2 | 19 | 38 | N/A | Screw-In
GSL23/2 | GSL | GFL Screw-In | GSL23 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 23W lamp | N/A |  | 2 | 23 | 46 | N/A | Screw-In
GSL28/2 | GSL | GFL Screw-In | GSL28 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 28W lamp | N/A |  | 2 | 28 | 56 | N/A | Screw-In
GSL30/2 | GSL | GFL Screw-In | GSL30 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 30W lamp | N/A |  | 2 | 30 | 60 | N/A | Screw-In
GSL33/3 | GSL | GFL Screw-In | GSL33 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (3) 33W lamp | N/A |  | 3 | 33 | 99 | N/A | Screw-In
GSL17/3 | GSL | GFL Screw-In | GSL17 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (3) 17W lamp | N/A |  | 3 | 17 | 51 | N/A | Screw-In
GSL19/3 | GSL | GFL Screw-In | GSL19 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (3) 19W lamp | N/A |  | 3 | 19 | 57 | N/A | Screw-In
GSL23/3 | GSL | GFL Screw-In | GSL23 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (3) 23W lamp | N/A |  | 3 | 23 | 69 | N/A | Screw-In
GSL28/3 | GSL | GFL Screw-In | GSL28 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (3) 28W lamp | N/A |  | 3 | 28 | 84 | N/A | Screw-In
GSL33/4 | GSL | GFL Screw-In | GSL33 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (4) 33W lamp | N/A |  | 4 | 33 | 132 | N/A | Screw-In
GSL17/4 | GSL | GFL Screw-In | GSL17 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (4) 17W lamp | N/A |  | 4 | 17 | 68 | N/A | Screw-In
GSL23/4 | GSL | GFL Screw-In | GSL23 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (4) 23W lamp | N/A |  | 4 | 23 | 92 | N/A | Screw-In
GSL33/5 | GSL | GFL Screw-In | GSL33 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (5) 33W lamp | N/A |  | 5 | 33 | 165 | N/A | Screw-In
GSL17/5 | GSL | GFL Screw-In | GSL17 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (5) 17W lamp | N/A |  | 5 | 17 | 85 | N/A | Screw-In
GSL46/1 | GSL | GFL Screw-In | GSL46 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 46W lamp | N/A |  | 1 | 46 | 46 | N/A | Screw-In
GSL69/1 | GSL | GFL Screw-In | GSL69 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 69W lamp | N/A |  | 1 | 69 | 69 | N/A | Screw-In
GSL12/1 | GSL | GFL Screw-In | GSL12 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 12W lamp | N/A |  | 1 | 12 | 12 | N/A | Screw-In
GSL24/1 | GSL | GFL Screw-In | GSL24 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 24W lamp | N/A |  | 1 | 24 | 24 | N/A | Screw-In
GSL34/1 | GSL | GFL Screw-In | GSL34 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 34W lamp | N/A |  | 1 | 34 | 34 | N/A | Screw-In
GSL41/1 | GSL | GFL Screw-In | GSL41 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 41W lamp | N/A |  | 1 | 41 | 41 | N/A | Screw-In
GSL9/1 | GSL | GFL Screw-In | GSL9 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 9W lamp | N/A |  | 1 | 9 | 9 | N/A | Screw-In
GSL69/2 | GSL | GFL Screw-In | GSL69 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 69W lamp | N/A |  | 2 | 69 | 138 | N/A | Screw-In
GSL24/2 | GSL | GFL Screw-In | GSL24 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 24W lamp | N/A |  | 2 | 24 | 48 | N/A | Screw-In
GSL34/2 | GSL | GFL Screw-In | GSL34 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 34W lamp | N/A |  | 2 | 34 | 68 | N/A | Screw-In
GSL41/2 | GSL | GFL Screw-In | GSL41 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 41W lamp | N/A |  | 2 | 41 | 82 | N/A | Screw-In

## Summary
2021 TRM Appendix C: Lighting Audit & Design Tool for Commercial and Industrial Projects
SUMMARY
Project / Site Information
| Applicant Name: |  |  |  | Construction Type: |  | . | .
| Customer Contact: |  |  |  | Building Type: |  | . | .
| Installation Address: |  |  |  | Facility Size:
Total Savings
|  | Change in Connected Load | Peak Demand Savings | Annual Energy Savings
| Lighting Only | 0 | 0 | 0
| Controls Only | - | 0 | 0
| Total | 0 | 0 | 0
Fixture and Sensor Summary
| Fixtures Installed: | 0 | Wattage Controlled by Newly Installed Lighting Controls:
| Lamps Installed: | 0 |  |  |  | 0
| Fixtures Removed: | 0
| Lamps Removed: | 0

## Lookups
2021 TRM Appendix C: Lighting Audit & Design Tool for Commercial and Industrial Projects
LOOKUPS
|  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
| HOU, CF, and IF by Facility Type | 2: Screw-Based CFL & LED; 4: Other General Service Lighting; 6: All Bulb Types 0% Electric Heat; 8: All Bulb Types 100% Electric Heat | IF by Space Cooling Type |  |  | SVG by Control Type |  |  | Schedule Names | LED Code Builder |  |  | Space-by-Space LPD Option Configurator Adapted from IECC 2015 Table C405.4.2
| Facility Type | HOU | CF | HOU | CF | IFenergy | IFdemand | IFenergy | IFdemand | Facility Type | IFenergy | IFdemand | Control Type | Code | SVG |  | DLC Listing Type | Length | Code | Space Type | Unit | Facility for Visually Impaired | Convention center | Dining: bar lounge/leisure | Dining: cafeteria/fast food | Dining: family | Gymnasium | Health-care clinic | Hospital | Hotel | Library | Manufacturing - 1 Shift | Manufacturing - 2 Shift | Manufacturing - 3 Shift | Motion picture theater | Museum | Penitentiary | Performing arts theater | Post Office | Religious building | Retail | School/university | Sports arena | Transportation | Warehouse | Other | Available List
| Education | 2944 | 0.39 | 2371 | 0.45 | 0.031323 | 0.19219 | -0.14228 | 0.19219 | Freezer | 0.5 | 0.5 | Light Switch | S_LS | 0% |  | 24" Linear Fluorescent Tube Replacement, Type A | 2 | LTA
| Exterior | 3604 | 0.11 | 3604 | 0.11 | 0 | 0 | 0 | 0 | Med. Temp. Refrg. | 0.29 | 0.29 | Occupancy Sensors | O_OS | 24% |  | 24" Linear Fluorescent Tube Replacement, Type B | 2 | LTB
| Exterior, Photocell-Controlled | 4306 | 0.11 | 4306 | 0.11 | 0 | 0 | 0 | 0 | High Temp. Refrg. | 0.18 | 0.18 | Time Clocks | O_TC | 24% |  | 24" Linear Fluorescent Tube Replacement, Type C | 2 | LTC | Airport Concourse | [23 empty] | 0.36
| Grocery | 7798 | 0.99 | 6471 | 0.93 | 0.031323 | 0.19219 | -0.14228 | 0.19219 | Unconditioned | 0 | 0 | Energy Management System | O_EMS | 24% |  | 36" Linear Fluorescent Tube Replacement, Type A | 3 | LTA | Atrium, < 40 ft. in height | [25 empty] | 0.03 | X
| Health | 2476 | 0.47 | 2943 | 0.52 | 0.031323 | 0.19219 | -0.14228 | 0.19219 |  |  |  | Photosensors | DL_PS | 28% |  | 36" Linear Fluorescent Tube Replacement, Type B | 3 | LTB | Atrium, >= 40 ft. in height | [25 empty] | 0.02 | X
| Industrial/Manufacturing - 1 Shift | 2857 | 0.96 | 2857 | 0.96 | 0.031323 | 0.19219 | -0.14228 | 0.19219 |  |  |  | Time Clocks | DL_TC | 28% |  | 36" Linear Fluorescent Tube Replacement, Type C | 3 | LTC | Audience Seating Area |  |  | 0.82 |  |  |  | 0.65 | [7 empty] | 1.14 |  | 0.28 | 2.43 |  | 1.53 |  | 0.63 | 0.43 |  |  | 0.43 | X
| Industrial/Manufacturing - 2 Shift | 4730 | 0.96 | 4730 | 0.96 | 0.031323 | 0.19219 | -0.14228 | 0.19219 |  |  |  | Dimmers | PT_DIM | 31% |  | 48" Linear Fluorescent Tube Replacement, Type A | 4 | LTA | Baggage/Carousel | [23 empty] | 0.53
| Industrial/Manufacturing - 3 Shift | 6631 | 0.96 | 6631 | 0.96 | 0.031323 | 0.19219 | -0.14228 | 0.19219 |  |  |  | Wireless on-off switches | PT_WS | 31% |  | 48" Linear Fluorescent Tube Replacement, Type B | 4 | LTB | Bank Activity Area | [25 empty] | 1.01 | X
| Institutional/Public Service | 1456 | 0.23 | 1419 | 0.23 | 0.031323 | 0.19219 | -0.14228 | 0.19219 |  |  |  | Bi-level switches | PT_BLS | 31% |  | 48" Linear Fluorescent Tube Replacement, Type C | 4 | LTC | Chapel |  | 2.21
| Lodging | 2925 | 0.38 | 3579 | 0.45 | 0.031323 | 0.19219 | -0.14228 | 0.19219 | IF for Comfort Cooled Spaces by Heating Fuel Type |  |  | Computer based controls | PT_CC | 31% | 0 | 96" Linear Fluorescent Tube Replacement, Type A | 8 | LTA | Class I Facility Playing Area | [22 empty] | 3.68
| Miscellaneous / Other | 2001 | 0.33 | 2830 | 0.58 | 0.031323 | 0.19219 | -0.14228 | 0.19219 |  |  |  | Pre-set scene selection | PT_PSS | 31% | Space Types | 96" Linear Fluorescent Tube Replacement, Type B | 8 | LTB | Class II Facility Playing Area | [22 empty] | 2.4
| Multi-Family Common Areas | 5950 | 0.73 | 5950 | 0.73 | 0.031323 | 0.19219 | -0.14228 | 0.19219 | Facility Type | IFenergy | IFdemand | Dimmable ballasts | IT_DIM | 36% |  | 96" Linear Fluorescent Tube Replacement, Type C | 8 | LTC | Class III Facility Playing Area | [22 empty] | 1.8
| Office | 1420 | 0.26 | 2294 | 0.48 | 0.031323 | 0.19219 | -0.14228 | 0.19219 | Non-Electric | 0.031 | 0.192 | On-off or dimmer switches for non-personal tuning | IT_DIM | 36% |  | Troffer LED Panel |  | TLP | Class IV Facility Playing Area | [22 empty] | 1.2
| Parking Garage | 8678 | 0.98 | 8678 | 0.98 | 0.031323 | 0.19219 | -0.14228 | 0.19219 | Electric | -0.142 | 0.192 | Occupancy and personal tuning/daylighting and occupancy | MT | 38% |  | High-Bay Luminaires |  | HBR | Classroom | [16 empty] | 1.34 | [8 empty] | 1.24 | X
| Restaurant | 3054 | 0.55 | 4747 | 0.77 | 0.031323 | 0.19219 | -0.14228 | 0.19219 | Unknown | 0 | 0.192 | <Name your custom Control type> | C_1 | 0% |  | Outdoor Pole/Arm-Mounted Luminaires |  | OP/A | Computer Room | [25 empty] | 1.71 | X
| Retail | 2383 | 0.56 | 2915 | 0.66 | 0.031323 | 0.19219 | -0.14228 | 0.19219 |  |  |  | <Name your custom Control type> | C_2 | 0% |  | Outdoor Wall-Mounted Luminaires |  | OW | Conference/Multipurpose Room | [25 empty] | 1.23 | X
| Street Lighting |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  |  | <Name your custom Control type> | C_3 | 0% |  | Refrigerated Display Case Luminaires |  | RDL | Convention Center/Exhibit Space |  |  | 1.45
| Warehouse | 2815 | 0.5 | 2545 | 0.48 | 0.031323 | 0.19219 | -0.14228 | 0.19219 |  |  |  | <Name your custom Control type> | C_4 | 0% |  | Street Lamp Luminaires |  | ST | Copy/Print Room | [25 empty] | 0.72 | X
| TRM Interior | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | <Name your custom Control type> | C_5 | 0% |  | Custom |  | C | Corridor |  | 0.92 | [6 empty] | 0.79 |  |  | 0.41 | 0.41 | 0.41 | [11 empty] | 0.66 | X
| TRM Exterior | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | Custom control types and corresponding SVG assumptions may be substituted when EDC data gathering (metering) produces more accurate/reliable SVG estimates. | [6 empty] | Courtroom | [25 empty] | 1.72 | X
| TRM Refrigeration | 6205 | 0.92 | 6205 | 0.92 | - | - | - | - | [10 empty] | Detailed Manufacturing Area | [11 empty] | 1.29 | 1.29 | 1.29
| TRM Exit | 8760 | 1 | 8760 | 1 | 0.031323 | 0.19219 | -0.14228 | 0.19219 | [10 empty] | Dining Area |  | 1.9 |  | 1.07 | 0.65 | 0.89 | [10 empty] | 0.96 | [8 empty] | 0.65 | X
| Values written in blue were not collected as part of the Commercial Light Metering Study and have been populated with 2021 TRM values. Values in cells with blue shading will not populate unless EDC is specified in cell D18 of the "General Information" tab. | [18 empty] | Dormitory/Living Quarters | [25 empty] | 0.38 | X
[20 empty] | Dressing Room | [17 empty] | 0.61
[20 empty] | Dressing/Fitting Room | [20 empty] | 0.71
| Lighting Power Density Allowances Space-by-Space Method | 5: Lighting Power Density Allowances Building Area Method |  |  |  | New Construction SVG Accountability | [6 empty] | Electrical/Mechanical Room | [25 empty] | 0.95 | X
[20 empty] | Elevator Lobby | [25 empty] | 0.64 | X | bar: 2 to 3; 5 to 9
| IECC 2015 Available Space Types for Selected Building Type | LPD Allowance | Unit |  | IECC 2015 Building Type |  |  | LPD | SWE Facility Type |  |  |  | Facility Type | % Req. | NC SVG |  |  |  |  | Emergency Vehicle Garage | [25 empty] | 0.56 | X
[13 empty] | Education | 69% | 16.56% |  |  |  |  | Equipment Room | [11 empty] | 0.74 | 0.74 | 0.74
| NEW CONSTRUCTION WHOLE BUILDING | 5: Automotive facility; 8: 0.8; 9: Miscellaneous / Other |  |  |  | Exterior | - | 0% |  |  |  |  | Exam/Treatment Room | [7 empty] | 1.66 | 1.66
11 | Atrium, < 40 ft. in height | 5: Convention center; 8: 1.01; 9: Miscellaneous / Other |  |  |  | Grocery | 20% | 4.8% |  |  |  |  | Extra High Bay Area, Greater than 50' Ceiling | [11 empty] | 1.05 | 1.05 | 1.05
12 | Atrium, >= 40 ft. in height | 5: Courthouse; 8: 1.01; 9: Institutional/Public Service |  |  |  | Health | 32% | 7.68% |  |  |  |  | Fellowship Hall | [19 empty] | 0.64
13 | Audience Seating Area | 5: Dining: bar lounge/leisure; 8: 1.01; 9: Restaurant |  |  |  | Industrial/Manufacturing - 1 Shift | - | 0% | 0 |  |  |  | Fire Station/Sleeping Quarters | [25 empty] | 0.22 | X
15 | Bank Activity Area | 5: Dining: cafeteria/fast food; 8: 0.9; 9: Restaurant |  |  |  | Industrial/Manufacturing - 2 Shift | - | 0% |  |  |  |  | Food Preparation Area | [25 empty] | 1.21 | X
21 | Classroom | 5: Dining: family; 8: 0.95; 9: Restaurant |  |  |  | Industrial/Manufacturing - 3 Shift | - | 0% |  |  |  |  | General Exhibition Area | [15 empty] | 1.05
22 | Computer Room | 5: Dormitory; 8: 0.57; 9: Education |  |  |  | Institutional/Public Service | 51% | 12.24% |  |  |  |  | Guest Room | [25 empty] | 0.47 | X
23 | Conference/Multipurpose Room | 5: Exercise center; 8: 0.84; 9: Health |  |  |  | Lodging | 61% | 14.64% |  |  |  |  | Gymnasium Exercise Area | [6 empty] | 0.72
25 | Copy/Print Room | 5: Exterior; 9: Exterior |  |  |  | Miscellaneous / Other | 24% | 5.76% |  |  |  |  | Gymnasium Play Area | [6 empty] | 1.2
26 | Corridor | 5: Exterior, Photocell-Controlled; 9: Exterior, Photocell-Controlled |  |  |  | Office | 62% | 14.88% |  |  |  |  | High Bay Area, 25' to 50' Ceiling | [11 empty] | 1.23 | 1.23 | 1.23
27 | Courtroom | 5: Fire Station; 8: 0.67; 9: Institutional/Public Service |  |  |  | Parking Garage | - | 0% |  |  |  |  | Imaging Room | [7 empty] | 1.51 | 1.51
29 | Dining Area | 5: Grocery; 8: 1.26; 9: Grocery |  |  |  | Restaurant | 21% | 5.04% |  |  |  |  | Laboratory | [21 empty] | 1.43 |  |  |  | 1.81 | X
30 | Dormitory/Living Quarters | 5: Gymnasium; 8: 0.94; 9: Health |  |  |  | Retail | 21% | 5.04% |  |  |  |  | Laundry/Washing Area | [25 empty] | 0.6 | X
33 | Electrical/Mechanical Room | 5: Health-care clinic; 8: 0.9; 9: Health |  |  |  | Warehouse | 60% | 14.4% |  |  |  |  | Library Reading Area | [10 empty] | 1.06
34 | Elevator Lobby | 5: Hospital; 8: 1.05; 9: Health |  |  |  | <Name your custom Facility type> |  | 0% |  |  |  |  | Library Stacks | [10 empty] | 1.71
35 | Emergency Vehicle Garage | 5: Hotel; 8: 0.87; 9: Lodging |  |  |  | <Name your custom Facility type> |  | 0% |  |  |  |  | Loading dock, interior | [25 empty] | 0.47 | X
40 | Fire Station/Sleeping Quarters | 5: Library; 8: 1.19; 9: Institutional/Public Service |  |  |  | <Name your custom Facility type> |  | 0% |  |  |  |  | Lobby |  | 1.8 | [7 empty] | 1.06 |  |  |  |  | 0.59 |  |  | 2 | [7 empty] | 0.9 | X
41 | Food Preparation Area | 5: Manufacturing - 1 Shift; 8: 1.17; 9: Industrial/Manufacturing - 1 Shift |  |  |  | <Name your custom Facility type> |  | 0% |  |  |  |  | Locker Room | [25 empty] | 0.75 | X
43 | Guest Room | 5: Manufacturing - 2 Shift; 8: 1.17; 9: Industrial/Manufacturing - 2 Shift |  |  |  | <Name your custom Facility type> |  | 0% |  |  |  |  | Lounge/Breakroom | [7 empty] | 0.92 | 0.92 | [16 empty] | 0.73 | X
48 | Laboratory | 5: Manufacturing - 3 Shift; 8: 1.17; 9: Industrial/Manufacturing - 3 Shift |  |  |  | % Req. column dictates the percentage of the total area of each building type found to be a space type requiring occupancy sensors by code per the Commercial Light Metering Study. | [6 empty] | Low Bay Area, Less than 25' Ceiling | [11 empty] | 1.19 | 1.19 | 1.19
49 | Laundry/Washing Area | 5: Motel; 8: 0.87; 9: Lodging | [10 empty] | Mall Concourse | [20 empty] | 1.1
52 | Loading dock, interior | 5: Motion picture theater; 8: 0.76; 9: Miscellaneous / Other | [10 empty] | Medical Supply Room | [7 empty] | 0.74 | 0.74
53 | Lobby | 5: Multifamily; 8: 0.51; 9: Lodging |  |  |  | Custom facility types and corresponding SVG assumptions may be substituted when default assumptions are not reflective of code baseline conditions. | [6 empty] | Nursery | [7 empty] | 0.88 | 0.88
54 | Locker Room | 5: Museum; 8: 1.02; 9: Institutional/Public Service | [10 empty] | Nurse's Station | [7 empty] | 0.71 | 0.71
55 | Lounge/Breakroom | 5: Office; 8: 0.82; 9: Office | [10 empty] | Office, Enclosed | [25 empty] | 1.11 | X
61 | Office, Enclosed | 5: Parking garage; 8: 0.21; 9: Parking Garage | [10 empty] | Office, Open | [25 empty] | 0.98 | X
62 | Office, Open | 5: Penitentiary; 8: 0.81; 9: Institutional/Public Service | [10 empty] | Operating Room | [7 empty] | 2.48 | 2.48
64 | Parking Area, Interior | 5: Performing arts theater; 8: 1.39; 9: Miscellaneous / Other | [10 empty] | Parking Area, Interior | [25 empty] | 0.19 | X
66 | Pharmacy Area | 5: Police station; 8: 0.87; 9: Institutional/Public Service | [10 empty] | Patient Room | [7 empty] | 0.62 | 0.62
71 | Restroom | 5: Post office; 8: 0.87; 9: Institutional/Public Service | [10 empty] | Pharmacy Area | [25 empty] | 1.68 | X
72 | Sales Area | 5: Religious building; 8: 1; 9: Institutional/Public Service | [10 empty] | Physical Therapy Room | [7 empty] | 0.91 | 0.91
73 | Seating Area, General | 5: Retail; 8: 1.26; 9: Retail | [10 empty] | Recovery Room | [7 empty] | 1.15 | 1.15
75 | Stairway | 5: School/university; 8: 0.87; 9: Education | [10 empty] | Recreation Room |  | 2.41
78 | Storage Room | 5: Sports arena; 8: 0.91; 9: Miscellaneous / Other | [10 empty] | Restoration Room | [15 empty] | 1.02
80 | Vehicular Maintenance Area | 5: Street Lighting; 9: Street Lighting | [10 empty] | Restroom |  | 1.21 | [23 empty] | 0.98 | X
81 | Workshop | 5: Town hall; 8: 0.89; 9: Institutional/Public Service | [10 empty] | Sales Area | [25 empty] | 1.59 | X
84 | Base Site Allowance | 3: Site; 5: Transportation; 8: 0.7; 9: Miscellaneous / Other | [10 empty] | Seating Area, General | [25 empty] | 0.54 | X
85 | Uncovered Parking Areas and Drives | 5: Warehouse; 8: 0.66; 9: Warehouse | [10 empty] | Sorting Room | [18 empty] | 0.94
86 | Building Grounds, Walkways less than 10' Wide | 3: Linear Ft; 5: Workshop; 8: 1.19; 9: Industrial/Manufacturing - 1 Shift | [10 empty] | Stairway | [25 empty] | 0.69 | X
87 | Building Grounds, Walkways 10' Wide or Greater | 5: Values written in blue were added for functionality reasons and are not directly from IECC. | [10 empty] | Storage Area for Medium to Bulky (Palletized) Items | [24 empty] | 0.58
88 | Building Grounds, Stairways | [18 empty] | Storage Area for Smaller Hand-Carried Items | [24 empty] | 0.95
89 | Building Grounds, Pedestrian Tunnels | [18 empty] | Storage Room | [25 empty] | 0.63 | X
90 | Building Entrances, Main Entries | 3: Linear Foot of Door Width | [10 empty] | Terminal Ticket Counter | [23 empty] | 0.8
91 | Building Entrances, Other Doors | 3: Linear Foot of Door Width | [10 empty] | Vehicular Maintenance Area | [25 empty] | 0.67 | X
92 | Building Entrances, Entry Canopies | [18 empty] | Workshop | [25 empty] | 1.59 | X
93 | Sales Canopies | [18 empty] | Worship/Pulpit/Choir Area | [19 empty] | 1.53
94 | Outdoor Sales, Open Areas | [18 empty] | Exterior Space Types | Unit | [25 empty] | Available List
95 | Outdoor Sales, Street Frontage | 3: Linear Foot of Frontage | [10 empty] | Base Site Allowance | Site | 500 | 600 | 750 | 1300 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
96 | Building Facades | 3: S.F. of gross above-grade wall area | [10 empty] | Uncovered Parking Areas and Drives |  | 0.04 | 0.06 | 0.1 | 0.13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
97 | ATM and Night Depositories, First Location | 3: Location | [10 empty] | Building Grounds, Walkways less than 10' Wide | Linear Ft | 0.7 | 0.7 | 0.8 | 1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
98 | ATM and Night Depositories, Additional Locations | 3: Location | [10 empty] | Building Grounds, Walkways 10' Wide or Greater |  | 0.14 | 0.14 | 0.16 | 0.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
99 | Entrances & Gatehouse Inspection Stations at Guarded Facilities | [18 empty] | Building Grounds, Stairways |  | 0.75 | 1 | 1 | 1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
100 | Loading Areas for Law Enforcement and Emergency Vehicles | [18 empty] | Building Grounds, Pedestrian Tunnels |  | 0.15 | 0.15 | 0.2 | 0.3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
101 | Drive-Up Windows & Doors | 3: Drive Through | [10 empty] | Building Entrances, Main Entries | Linear Foot of Door Width | 20 | 20 | 30 | 30 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
102 | Parking Near 24-Hour Retail Entrances | 3: Main Entry | [10 empty] | Building Entrances, Other Doors | Linear Foot of Door Width | 20 | 20 | 20 | 20 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
[20 empty] | Building Entrances, Entry Canopies |  | 0.25 | 0.25 | 0.4 | 0.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
[20 empty] | Sales Canopies |  | 0.6 | 0.6 | 0.8 | 1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
[20 empty] | Outdoor Sales, Open Areas |  | 0.25 | 0.25 | 0.5 | 0.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
[20 empty] | Outdoor Sales, Street Frontage | Linear Foot of Frontage | 0 | 10 | 10 | 30 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
[20 empty] | Building Facades | S.F. of gross above-grade wall area | 0 | 0.075 | 0.113 | 0.15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
[20 empty] | ATM and Night Depositories, First Location | Location | 270 | 270 | 270 | 270 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
[20 empty] | ATM and Night Depositories, Additional Locations | Location | 90 | 90 | 90 | 90 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
[20 empty] | Entrances & Gatehouse Inspection Stations at Guarded Facilities |  | 0.75 | 0.75 | 0.75 | 0.75 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
[20 empty] | Loading Areas for Law Enforcement and Emergency Vehicles |  | 0.5 | 0.5 | 0.5 | 0.5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
[20 empty] | Drive-Up Windows & Doors | Drive Through | 400 | 400 | 400 | 400 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
[20 empty] | Parking Near 24-Hour Retail Entrances | Main Entry | 800 | 800 | 800 | 800 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
Individual Lighting Power Allocances for Building Exteriors Adapted from IECC 2015 Table C405.4.2(2)
| 55 | [18 empty] | Space Type | Unit | Zone 1 | Zone 2 | Zone 3 | Zone 4
[20 empty] | Base Site Allowance | Site | 500 | 600 | 750 | 1300
[20 empty] | Uncovered Parking Areas and Drives |  | 0.04 | 0.06 | 0.1 | 0.13
[20 empty] | Building Grounds, Walkways less than 10' Wide | Linear Ft | 0.7 | 0.7 | 0.8 | 1
[20 empty] | Building Grounds, Walkways 10' Wide or Greater |  | 0.14 | 0.14 | 0.16 | 0.2
[20 empty] | Building Grounds, Stairways |  | 0.75 | 1 | 1 | 1
[20 empty] | Building Grounds, Pedestrian Tunnels |  | 0.15 | 0.15 | 0.2 | 0.3
[20 empty] | Building Entrances, Main Entries | Linear Foot of Door Width | 20 | 20 | 30 | 30
[20 empty] | Building Entrances, Other Doors | Linear Foot of Door Width | 20 | 20 | 20 | 20
[20 empty] | Building Entrances, Entry Canopies |  | 0.25 | 0.25 | 0.4 | 0.4
[20 empty] | Sales Canopies |  | 0.6 | 0.6 | 0.8 | 1
[20 empty] | Outdoor Sales, Open Areas |  | 0.25 | 0.25 | 0.5 | 0.7
[20 empty] | Outdoor Sales, Street Frontage | Linear Foot of Frontage | 0 | 10 | 10 | 30
[20 empty] | Building Facades | S.F. of gross above-grade wall area | 0 | 0.075 | 0.113 | 0.15
[20 empty] | ATM and Night Depositories, First Location | Location | 270 | 270 | 270 | 270
[20 empty] | ATM and Night Depositories, Additional Locations | Location | 90 | 90 | 90 | 90
[20 empty] | Entrances & Gatehouse Inspection Stations at Guarded Facilities |  | 0.75 | 0.75 | 0.75 | 0.75
[20 empty] | Loading Areas for Law Enforcement and Emergency Vehicles |  | 0.5 | 0.5 | 0.5 | 0.5
[20 empty] | Drive-Up Windows & Doors | Drive Through | 400 | 400 | 400 | 400
[20 empty] | Parking Near 24-Hour Retail Entrances | Main Entry | 800 | 800 | 800 | 800