## Manual
Pennsylvania Act 129 Motor & VFD Audit and Design Tool
MANUAL
Table of Contents:
I. Purpose
II. Organization
III. User Guide
IV. Disclaimer
I. Purpose
The purpose of the Motor & VFD Audit and Design Tool is two-fold:
1. To document the pre- and post-installation cases.
2. To facilitate the calculation of energy savings and demand reduction for motor and VFD installations.
II. Organization
The Motor & VFD Audit and Design Tool is organized into 6 sheets.
(1) Manual
The "Manual" sheet contains the instruction manual for using the Motor & VFD Audit and Design Tool.
(2) Changelog
The "Changelog" sheet provides a brief description of major changes from the previous version.
(3) General Information
The "General Information" sheet should be populated with basic information about the project, like project and facility name. Fields for Utility, Facility Type, and Weather Location are necessary to properly pull in default values from the TRM.
(4) 3.3.1 Premium Efficiency Motors
The "3.3.1 Premium Efficiency Motors" sheet collects all relevant information to calculate energy savings and peak demand reduction for motor replacements. This form follows the conventions and equations described in the PA TRM and facilitates the calculation of gross energy savings for evaluation purposes. Note that the requirements of Section 3.3.1 (Premium Efficiency Motors) in the 2021 TRM restrict the protocol to only motor replacements without VFDs. This form must be used to calculate savings for motor replacement measures only (i.e. replacement of old motors with new energy efficient motors of the same rated horsepower).
The energy efficiency motor and configuration details should be entered in the "Post-Retrofit Details" section (columns E-N). Baseline motor efficiency will be automatically populated using tables as defined in the 2021 TRM. The energy and peak demand savings resulting from the motor replacement alone will be automatically calculated in cells AD6 and AC6 respectively. To calculate savings resulting from VFD measures, refer to the notes described below.
(5) 3.3.2 VFD Improvements
The "3.3.2 VFD Improvements" sheet collects all relevant information to calculate energy savings and peak demand reduction for VFDs. This form follows the conventions and equations described in the PA TRM and facilitates the calculation of gross energy savings for evaluation purposes. This form must be used to calculate savings for VFD measures only, not the combination of new motors and VFDs.
The motor and configuration details should be entered in the "Post-Retrofit Details" section (Columns E-N) for a motor with VFD. A custom motor load profile can be selected if the appropriate fields are populated on the 'VFD Custom Load Profile' tab. Select the baseline control configuration from the pull down menu in Column O. The energy and peak demand savings resulting from installation of a VFD will be automatically calculated in cells BF6 and BE6 respectively. Note that custom protocols must be followed if the existing motor already has a VFD installed or if the VFD Baseline is not listed in the options.
(6) VFD Custom Load Profile
The "VFD Custom Load Profile" sheet should be used to define custom fan or pump load profiles for a VFD project. Up to 10 custom profiles can be entered.
(7) Lookups
This tab houses lookup tables used in both the motor and VFD calculation worksheets. Tables taken from the TRM include default hours of use and motor baseline efficiency.
III. User Guide
The tool contains all information regarding motors and VFDs required for the calculation of savings pursuant to the PA TRM. The use of this tool is encouraged but not required. Users of the Motor and VFD Audit and Design Tool must complete the "Motor Inventory" and/or "VFD Inventory" depending on the measures installed for the project. For VFD measures in conjunction with a motor replacement measure, the savings must be calculated separately using the "Motor Form" and "VFD Form". To find out how to calculate savings resulting from motor replacement and VFD measures separately, refer to the notes described above. The designer must select the appropriate facility type, utility, and weather file from the drop down menu. Use one line for each unique motor, i.e. motors with different operating conditions or different motor specifications. Complete all green fields to calculate the peak demand reduction and annual energy savings. Gray fields are computed automatically. Roll mouse over the field heading for additional help. Projects with facility types or motor functions not included on the drop down menu must follow custom protocols to determine appropriate run hours and coincidence factor values. Motor replacements with the following conditions should also follow custom protocols:
* Variable frequency drive (VFD) control on the existing (baseline) motor
* Two-speed motor (existing and/or new)
* Single speed motor with variable loading (not standard)
* Industrial process applications
* Applications where the building type or motor usage group is not listed in Table 3-67 through 3-71 of the 2021 TRM
* New motor has a different rated horsepower than the existing motor
* Change in annual operating hours is anticipated
IV. Disclaimer
This document does not modify any requirements of the PA TRM and is provided for convenience only. If any discrepancy between the TRM and this document exist, the TRM should be followed.

## Changelog
Pennsylvania Act 129 Lighting Audit and Design Tool
CHANGELOG
Version 7 (Effective June 3, 2010)
1) | Released with TRM Order in June 2010
Version 8 (Submitted October 27, 2011. Effective June 1, 2011)
1) | Created Changelog
2) | Revised "Manual" and "Glossary" to improve user guide and increase usability
3) | Revised "Manual" and "Glossary" to reflect new changes to the TRM
Version 9 (Submitted September 13, 2011 for 2012 TRM Tentative Order)
1) | In "Motor and VFD Form", revised formulas in Columns O, P, and S to correct referencing errors
2) | In "Motor and VFD Form", added Column Q (Full Load kW) to correct a calculation error incorrectly applying DSF
3) | In "Motor and VFD Form", revised Column G (Coincidence Factor) to reflect TRM values (0.74 for single, 0.37 for duplex)
4) | In "Glossary", revised definition of coincidence factor to reflect above change.
5) | In "Glossary", added definition for "Full Load kW"
6) | In "Glossary", revised definition of "Nominal Efficiency" to reflect ability to custom input efficiency values for the new motor efficiency and baseline motor efficiency if the new motor is for new construction or replace on burnout.
7) | In "Manual", updated TRM reference from Table 6-12 to Table 3-15
Version 10 (Submitted December 5, 2011 for 2012 TRM Final Order)
1) | In "Motor and VFD Form", updated operating hours lookup table to reflect TRM table.
2) | In "Motor and VFD Form", corrected formulas for efficiency lookups, post-installation peak kW calculation, and total kWh calculation for post-installation line item #7.
3) | In "Motor and VFD Form", updated form to include new ESF and DSF values.
4) | In "Glossary", updated entries to reflect new column O and definition of "baseline".
Version 11 (Submitted August 31, 2012 for 2013 TRM Tentative Order)
1) | Created "Motor Form" and "VFD Form" to calculate savings for motors and VFD measures separately to be consistent with TRM protocols.
2) | In "Motor Form" and "VFD Form", updated operating hours lookup table to reflect TRM table.
3) | In "VFD Form", updated ESF and DSF values lookup table to reflect TRM table.
3) | Revised "Manual" and "Glossary" to reflect new changes to the TRM and Appendix D
Version 12 (Submitted December 07, 2012 for 2013 TRM Final Order)
1) | Changed the definition of "Load Factor" in Glossary to be consistent with TRM protocols.
Version 13 (Submitted August 29, 2013 for 2014 TRM Tentative Order)
1) | Revised the algorithms in Column R of the "VFD Form" tab used to calculate energy and peak demand savings to be consistent with TRM protocols. Removed a conversion factor of 0.746 to convert from HP to kW.
Version 13 (Submitted December 05, 2013 for 2014 TRM Final Order)
1) | Updated motor efficiency tables to reflect new changes to the TRM.
2) | Removed motor efficiency tables from "VFD Form".
3) | Revised "Motor Form" and added "Motor Custom Input" to allow for addition of custom motor applications.
4) | Revised "Manual" and "Glossary" to reflect new changes to the TRM and Appendix D.
Version 14 (Submitted August 05, 2014)
1) | Updated motor efficiency tables to reflect new changes to the TRM.
2) | Updated "Coincidence Factor" , "Operating Hours" and "Facility Type" lookup tables to reflect new changes to the TRM.
3) | Formulas for Coincidence Factor and Operating hours are updated to reflect changes to the TRM.
4) | Consolidated all lookup tables under single tab "Lookup Tables"; updated references to lookup tables.
5) | Added "City" to the general information section for "Motor Form" , "VFD Form" , "Motor Custom Input" and "Summary"
6) | Linked general information cells of "Motor Form" , "VFD Form" and "Motor Custom Input" to cells in "Summary". Locked the cells to protect their links.
7) | Motor Configuration column is deleted from "Motor Form" and "VFD Form"
8) | Installation date cell is modified to allow entry of a date between 6/1/2015 and 5/31/2016 only. For all other dates , an error message is displayed.
9) | Program Year is limited to Program Year 7.
10) | "VFD on Motor" column is deleted from "VFD Form". The formulas for ESF, DSF and Full Load kW are updated to exclude the deleted column.
11) | "Full Load kW" on "VFD Form" revised - previously displayed a horsepower value. "Peak kW" and "Annual kWh" adjusted to account for change made to "Full Load kW."
12) | Introduced a macro button on "Motor Form" and "VFD Form" that increases number of motor line items for user's convenience.
13) | Added 900 RPM option to "Synchronous Speed" for "Motor Form", "VFD Form" and "Motor Custom Form."
14) | Revised "Manual" and "Glossary" to reflect new changes to the TRM and Appendix D.
15) | References to "Hot Water Pump" changed to "Heating Hot Water Pump" to be consistent with TRM. References to "HWP" changed to "HHWP."
Version 15 (Submitted February 20, 2015)
1) | Updated motor efficiency tables to reflect new changes to the TRM.
2) | Removed "Nema Design Type", "Synchronous Speed" and "Enclosure Type" fields from post-installation data in "Motor Form"
Version 16 (Submitted June 1, 2015)
1) Relocated "Summary" form before the other input forms
2) Updated selectable program years to reflect Phase III program years
3) Updated TRM table references in "Lookup Tables"
Version 17 (Submitted June 1, 2015)
1) Major revisions to the 'VFD Form' tab:
1.1) Renamed to '3.3.2 VFD Improvements'
1.2) Algorithms changed to reflect 2021 TRM. Instead of defined ESF/DSFs, new algorithm uses load profiles, and baseline and VFD part load factors.
1.3) Capability to define custom load profiles added. (See 'VFD Custom Load Profile' tab.) Default 'HVAC Fan' and 'HVAC Pump' profiles included.
2) Reformatted 'Motor Form' to align with new 'VFD Inventory' format, including name change to '3.3.1 Premium Efficiency Motors'
3) 'General Information' tab created to house basic project information.
Note on A77: Mary-Hall: Update date

## General Information
2020 TRM Appendix D: Motor & VFD Audit and Design Tool
GENERAL INFORMATION
| KEY: | Input Field |  |  | Example Cell |  | Cell Creating Error in Calculations
|  | Calculated Value |  |  | Intermediate Calc.
❶ Project / Site Information
Provide basic project information below.
Applicant Name:
Facility Name:
Installation Address:
| City: |  |  | State: |  | Zip:
| Utility: |  | Account No.:
Contact Name & Title:
Phone:
Email:
Facility Type:
Weather Location:
Installation Date:

## 3.3.1 Premium Efficiency Motors
2020 TRM Appendix D: Motor & VFD Audit and Design Tool
3.3.1 Premium Efficiency Motors
MOTORS Total
[27 empty] | 0 | 0
SAVINGS
|  |  | POST-RETROFIT DETAILS | [9 empty] | BASELINE DETAILS |  |  |  |  | Analysis | [8 empty] | MOTORS
Line Item | Unique Motor I.D.(s) | Motor Function | Manufacturer | Model Number | Motor Horsepower | NEMA Design Type | Number of Poles | Enclosure Type | Motor Efficiency | Number of Identical Units | Default Load Factor (LF) | Custom Load Factor (LF) | Default Annual Run Hours | Custom Annual Run Hours | Default Coincidence Factor | Custom Coincidence Factor | Baseline Nominal Efficiency | Analysis Hours | Analysis LF | Analysis CF | Base Full Load kW | Base Peak kW | Base Annual kWh | Energy Efficient Full Load kW | Energy Efficient Peak kW | Energy Efficient Annual kWh | Peak Demand (kW) | Energy (kWh) | Lamps Removed Counter | Lamps Installed Counter
Ex. | CHWP-1 | SF | Baldor | A12345 | 10 | NEMA Design A | 4 | ODP | 96% | 2 | 0.76 |  | N/A |  | 0 |  | 91.7% | N/A | 0.76 | 0 | 12.3655 | 0 |  | 11.8117 | 0 |  | 0
1 | [12 empty] | N/A |  | N/A |  | 0% | N/A |  | N/A
2 | [12 empty] | N/A |  | N/A |  | 0% | N/A |  | N/A
3 | [12 empty] | N/A |  | N/A |  | 0% | N/A |  | N/A
4 | [12 empty] | N/A |  | N/A |  | 0% | N/A |  | N/A
5 | [12 empty] | N/A |  | N/A |  | 0% | N/A |  | N/A
6 | [12 empty] | N/A |  | N/A |  | 0% | N/A |  | N/A
7 | [12 empty] | N/A |  | N/A |  | 0% | N/A |  | N/A
8 | [12 empty] | N/A |  | N/A |  | 0% | N/A |  | N/A
9 | [12 empty] | N/A |  | N/A |  | 0% | N/A |  | N/A
10 | [12 empty] | N/A |  | N/A |  | 0% | N/A |  | N/A
Note on I10: Mary-Hall: 3600 RPM 2 Pole 1800 RPM 4 Pole 1200 RPM 6 Pole 900 RPM 8 Pole
Note on M10: Mary-Hall: default value is 0.78 for pumps and 0.76 for fans
Note on N10: Mary-Hall: Use this column to overwrite the default.
Note on P10: Mary-Hall: Enter custom operating hours to override the default
Note on R10: Mary-Hall: Enter custom operating hours to override the default

## 3.3.2 VFD Improvements
2021 TRM Appendix D: Motor & VFD Audit and Design Tool
3.3.3 Variable Frequency Drive (VFD) Improvements
Total VFDs
[55 empty] | 0 | 0
SAVINGS
|  |  | POST-RETROFIT DETAILS | [9 empty] | BASELINE DETAILS | Load Profile | [11 empty] | Baseline Power Part Load Ratios | [10 empty] | VFD Power Part Load Ratios | [10 empty] | Analysis
Line Item | Unique Motor I.D.(s) | Motor Function | Manufacturer | Model Number | Motor Horsepower | Motor Efficiency | Default Load Factor (LF) | Custom Load Factor (LF) | Default Annual Run Hours | Custom Annual Run Hours | Load Profile | Avg Flow Fraction During Peak | Baseline Control Type | VFD Control Type | 0% | 10% | 20% | 30% | 40% | 50% | 60% | 70% | 80% | 90% | 100% | 0% | 10% | 20% | 30% | 40% | 50% | 60% | 70% | 80% | 90% | 100% | 0% | 10% | 20% | 30% | 40% | 50% | 60% | 70% | 80% | 90% | 100% | Analysis Hours | Analysis LF | Full Load kW | Base Peak kW | Base Annual kWh | Energy Efficient Peak kW | Energy Efficient Annual kWh | Peak Demand (kW) | Energy (kWh)
Ex. | SF-1 | SF | Baldor | A12345 | 10 | 90.5% | 0.76 |  | N/A |  | HVAC fan | 90% | Fan: Constant Volume | VFD Fan | 0% | 0% | 0% | 0% | 0% | 10% | 20% | 30% | 20% | 15% | 5% | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.0475 | 0.0475 | 0.0537 | 0.08 | 0.1289 | 0.2027 | 0.3038 | 0.4346 | 0.5975 | 0.795 | 1.0293 | N/A | 0.76 | 6.2648 | 6.2648 |  | 4.9805 |  | 1.2843
1 | [8 empty] | N/A |  |  | 90% | [35 empty] | N/A
2 | [8 empty] | N/A |  |  | 90% | [35 empty] | N/A
3 | [8 empty] | N/A |  |  | 90% | [35 empty] | N/A
4 | [8 empty] | N/A |  |  | 90% | [35 empty] | N/A
5 | [8 empty] | N/A |  |  | 90% | [35 empty] | N/A
6 | [8 empty] | N/A |  |  | 90% | [35 empty] | N/A
7 | [8 empty] | N/A |  |  | 90% | [35 empty] | N/A
8 | [8 empty] | N/A |  |  | 90% | [35 empty] | N/A
9 | [8 empty] | N/A |  |  | 90% | [35 empty] | N/A
10 | [8 empty] | N/A |  |  | 90% | [35 empty] | N/A
Note on I10: Mary-Hall: default value is 0.78 for pumps and 0.76 for fans
Note on J10: Mary-Hall: Use this column to overwrite the default.
Note on L10: Mary-Hall: Enter custom operating hours to override the default
Note on N10: Mary-Hall: Default is 90%

## VFD Custom Load Profile
2021 TRM Appendix D: Motor & VFD Audit and Design Tool
VFD Custom Load Profile Input
% Capacity | Default HVAC Fan | Default HVAC Pump | Custom Load Profile 1 | Custom Load Profile 2 | Custom Load Profile 3 | Custom Load Profile 4 | Custom Load Profile 5 | Custom Load Profile 6 | Custom Load Profile 7 | Custom Load Profile 8 | Custom Load Profile 9 | Custom Load Profile 10 | MOTORS | Total
0% | 0% | 0%
10% | 0% | 0%
20% | 0% | 0%
30% | 0% | 5%
40% | 0% | 10%
50% | 10% | 20%
60% | 20% | 30%
70% | 30% | 20%
80% | 20% | 10%
90% | 15% | 5%
100% | 5% | 0%
Total | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Note on E5: Mary-Hall: Load Profile can be renamed
Note on F5: Mary-Hall: Load profile can be renamed
Note on G5: Mary-Hall: Load profile can be renamed
Note on H5: Mary-Hall: Load Profile can be renamed
Note on I5: Mary-Hall: Load Profile can be renamed
Note on J5: Mary-Hall: Load Profile can be renamed
Note on K5: Mary-Hall: Load Profile can be renamed
Note on L5: Mary-Hall: Load Profile can be renamed
Note on M5: Mary-Hall: Load Profile can be renamed
Note on N5: Mary-Hall: Load Profile can be renamed
Note on E17: Mary-Hall: Total should equal 100%.
Note on F17: Mary-Hall: Total should equal 100%.
Note on G17: Mary-Hall: Total should equal 100%.

## Lookups
2021 TRM Appendix D: Motor & VFD Audit and Design Tool
LOOKUPS
[20 empty] | Tables 3-67 through 3-71 (Annual Run Hours) | [9 empty] | Tables 3-67 through 3-71 (CF) | [9 empty] | Table 3-73: Defaul Load Profiles for HVAC Fans and Pumps
|  |  |  | Table 3‑65: Baseline Efficiencies for NEMA Design A and NEMA Design B Motors | [8 empty] | Table 3‑66: Baseline Motor Nominal Full-Load Efficiencies for NEMA Design C Motors | [9 empty] | CHWP | CTF | CW Pump | HHWP | SF | [5 empty] | CHWP | CTF | CW Pump | HHWP | SF |  |  | Flow Fraction (%) | 0% | 10% | 20% | 30% | 40% | 50% | 60% | 70% | 80% | 90% | 100%
Motor Function | Default Load Profile | VFD Control Type | Default LF | HP | 2 Pole (3600 RPM) |  | 4 Pole (1800 RPM) |  | 6 Pole (1200 RPM) |  | 8 Pole (900 RPM) |  |  | 4 Pole (1800 RPM) |  | 6 Pole (1200 RPM) |  | 8 Pole (900 RPM) |  | Allentown | Education - College/University | Allentown Education - College/University | 4006.5 | 4005.5 | 5544 | 4548 | 6041.5 |  |  | Allentown | Education - College/University | Allentown Education - College/University | 0.405 | 0.405 | 0.61 | 0.005 | 0.425 |  | 2 | HVAC fan | 0% | 0% | 0% | 0% | 0% | 10% | 20% | 30% | 20% | 15% | 5% | 100%
CHWP | HVAC Pump | VFD Pump | 0.79 |  | Enclosed | Open | Enclosed | Open | Enclosed | Open | Enclosed | Open |  | Enclosed | Open | Enclosed | Open | Enclosed | Open | Allentown | Education - Other | Allentown Education - Other | 2721 | 2742 | 1735 | 3651 | 4380 |  |  | Allentown | Education - Other | Allentown Education - Other | 0.1 | 0.11 | 0.53 | 0 | 0.12 |  | 3 | HVAC Pump | 0% | 0% | 0% | 5% | 10% | 20% | 30% | 20% | 10% | 5% | 0% | 100%
CTF | HVAC Fan | VFD Fan | 0.76 |  | TEFC2 | ODP2 | TEFC4 | ODP4 | TEFC6 | ODP6 | TEFC8 | ODP8 | HP | TEFC4 | ODP4 | TEFC6 | ODP6 | TEFC8 | ODP8 | Allentown | Grocery | Allentown Grocery | #N/A | #N/A | #N/A | #N/A | 6708 |  |  | Allentown | Grocery | Allentown Grocery | #N/A | #N/A | #N/A | #N/A | 0.24 |  | 4 | Custom Load Profile 1 | [11 empty] | 0% | bar: 0% to 100%
CW Pump | HVAC Pump | VFD Pump | 0.79 | 1 | 77% | 77% | 85.5% | 85.5% | 82.5% | 82% | 75.5% | 75.5% | 1 | 85.5% | 85.5% | 82.5% | 82.5% | 75.5% | 75.5% | Allentown | Health - Hospital | Allentown Health - Hospital | 5588 | 5587 | 1781 | 8760 | 8760 |  |  | Allentown | Health - Hospital | Allentown Health - Hospital | 0.46 | 0.45 | 0.29 | 0.09 | 0.43 |  | 5 | Custom Load Profile 2 | [11 empty] | 0% | bar: 0% to 100%
HHWP | HVAC Pump | VFD Pump | 0.79 | 1.5 | 84% | 84% | 86.5% | 86.5% | 87.5% | 86.5% | 78.5% | 77% | 1.5 | 86.5% | 86.5% | 87.5% | 86.5% | 78.5% | 77% | Allentown | Health - Other | Allentown Health - Other | 3892 | 3894 | 2889 | 5934 | 8760 |  |  | Allentown | Health - Other | Allentown Health - Other | 0.24 | 0.24 | 0.46 | 0 | 0.24 |  | 6 | Custom Load Profile 3 | [11 empty] | 0% | bar: 0% to 100%
SF | HVAC Fan | VFD Fan | 0.76 | 2 | 85.5% | 85.5% | 86.5% | 86.5% | 88.5% | 87.5% | 84% | 86.5% | 2 | 86.5% | 86.5% | 88.5% | 87.5% | 84% | 86.5% | Allentown | Industrial Manufacturing | Allentown Industrial Manufacturing | 1735 | 1735 | 3527 | 1258 | 3831 |  |  | Allentown | Industrial Manufacturing | Allentown Industrial Manufacturing | 0.53 | 0.53 | 0.405 | 0 | 0.475 |  | 7 | Custom Load Profile 4 | [11 empty] | 0% | bar: 0% to 100%
|  |  |  | 3 | 86.5% | 85.5% | 89.5% | 89.5% | 89.5% | 88.5% | 85.5% | 87.5% | 3 | 89.5% | 89.5% | 89.5% | 88.5% | 85.5% | 87.5% | Allentown | Institutional/Public Service | Allentown Institutional/Public Service | #N/A | #N/A | #N/A | #N/A | 5188 |  |  | Allentown | Institutional/Public Service | Allentown Institutional/Public Service | #N/A | #N/A | #N/A | #N/A | 0.53 |  | 8 | Custom Load Profile 5 | [11 empty] | 0% | bar: 0% to 100%
Utility |  |  |  | 5 | 88.5% | 86.5% | 89.5% | 89.5% | 89.5% | 89.5% | 86.5% | 88.5% | 5 | 89.5% | 89.5% | 89.5% | 89.5% | 86.5% | 88.5% | Allentown | Lodging | Allentown Lodging | 5845 | 5844 | 2448 | 6469 | 8760 |  |  | Allentown | Lodging | Allentown Lodging | 0.61 | 0.61 | 0.11 | 0 | 0.64 |  | 9 | Custom Load Profile 6 | [11 empty] | 0% | bar: 0% to 100%
Duquesne Light |  |  |  | 7.5 | 89.5% | 88.5% | 91.7% | 91% | 91% | 90.2% | 86.5% | 89.5% | 7.5 | 91.7% | 91% | 91% | 90.2% | 86.5% | 89.5% | Allentown | Office | Allentown Office | 1789 | 1789 | 3950 | 3214 | 4195 |  |  | Allentown | Office | Allentown Office | 0.29 | 0.29 | 0.45 | 0 | 0.295 |  | 10 | Custom Load Profile 7 | [11 empty] | 0% | bar: 0% to 100%
Met-Ed (FirstEnergy) |  |  |  | 10 | 90.2% | 89.5% | 91.7% | 91.7% | 91% | 91.7% | 89.5% | 90.2% | 10 | 91.7% | 91.7% | 91% | 91.7% | 89.5% | 90.2% | Allentown | Restaurant | Allentown Restaurant | #N/A | #N/A | #N/A | #N/A | 6282 |  |  | Allentown | Restaurant | Allentown Restaurant | #N/A | #N/A | #N/A | #N/A | 0.375 |  | 11 | Custom Load Profile 8 | [11 empty] | 0% | bar: 0% to 100%
Penn Power (FirstEnergy) |  |  |  | 15 | 91% | 90.2% | 92.4% | 93% | 91.7% | 91.7% | 89.5% | 90.2% | 15 | 92.4% | 93% | 91.7% | 91.7% | 89.5% | 90.2% | Allentown | Retail | Allentown Retail | 2957 | 2957 | 3675 | 2676 | 5136.6667 |  |  | Allentown | Retail | Allentown Retail | 0.46 | 0.46 | 0.24 | 0 | 0.50333 |  | 12 | Custom Load Profile 9 | [11 empty] | 0% | bar: 0% to 100%
Penelec (FirstEnergy) |  |  |  | 20 | 91% | 91% | 93% | 93% | 91.7% | 92.4% | 90.2% | 91% | 20 | 93% | 93% | 91.7% | 92.4% | 90.2% | 91% | Allentown | Warehouse - Other | Allentown Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 5037 |  |  | Allentown | Warehouse - Other | Allentown Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 0.18 |  | 13 | Custom Load Profile 10 | [11 empty] | 0% | bar: 0% to 100%
West Penn Power (FirstEnergy) |  |  |  | 25 | 91.7% | 91.7% | 93.6% | 93.6% | 93% | 93% | 90.2% | 91% | 25 | 93.6% | 93.6% | 93% | 93% | 90.2% | 91% | Allentown | Warehouse - Refrigerated | Allentown Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 4041 |  |  | Allentown | Warehouse - Refrigerated | Allentown Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 0.5
PECO |  |  |  | 30 | 91.7% | 91.7% | 93.6% | 94.1% | 93% | 93.6% | 91.7% | 91.7% | 30 | 93.6% | 94.1% | 93% | 93.6% | 91.7% | 91.7% | Binghamton | Education - College/University | Binghamton Education - College/University | 3435.5 | 3435 | 4591 | 5270.5 | 6054 |  |  | Binghamton | Education - College/University | Binghamton Education - College/University | 0.265 | 0.26 | 0.58 | 0.005 | 0.3
PPL |  |  |  | 40 | 92.4% | 92.4% | 94.1% | 94.1% | 94.1% | 94.1% | 91.7% | 91.7% | 40 | 94.1% | 94.1% | 94.1% | 94.1% | 91.7% | 91.7% | Binghamton | Education - Other | Binghamton Education - Other | 1849 | 1851 | 1305 | 4251 | 4583 |  |  | Binghamton | Education - Other | Binghamton Education - Other | 0.08 | 0.08 | 0.4 | 0 | 0.08
|  |  |  | 50 | 93% | 93% | 94.5% | 94.5% | 94.1% | 94.1% | 92.4% | 92.4% | 50 | 94.5% | 94.5% | 94.1% | 94.1% | 92.4% | 92.4% | Binghamton | Grocery | Binghamton Grocery | #N/A | #N/A | #N/A | #N/A | 6764 |  |  | Binghamton | Grocery | Binghamton Grocery | #N/A | #N/A | #N/A | #N/A | 0.21
Facility Types |  |  |  | 60 | 93.6% | 93.6% | 95% | 95% | 94.5% | 94.5% | 92.4% | 93% | 60 | 95% | 95% | 94.5% | 94.5% | 92.4% | 93% | Binghamton | Health - Hospital | Binghamton Health - Hospital | 4801 | 4798 | 1389 | 8760 | 8760 |  |  | Binghamton | Health - Hospital | Binghamton Health - Hospital | 0.38 | 0.37 | 0.245 | 0.09 | 0.24
Education - College/University |  |  |  | 75 | 93.6% | 93.6% | 95.4% | 95% | 94.5% | 94.5% | 93.6% | 94.1% | 75 | 95.4% | 95% | 94.5% | 94.5% | 93.6% | 94.1% | Binghamton | Health - Other | Binghamton Health - Other | 3093 | 3093 | 2381 | 6627 | 8760 |  |  | Binghamton | Health - Other | Binghamton Health - Other | 0.2 | 0.2 | 0.33 | 0 | 0.21
Education - Other |  |  |  | 100 | 94.1% | 93.6% | 95.4% | 95.4% | 95% | 95% | 93.6% | 94.1% | 100 | 95.4% | 95.4% | 95% | 95% | 93.6% | 94.1% | Binghamton | Industrial Manufacturing | Binghamton Industrial Manufacturing | 1306 | 1306 | 2938 | 1684 | 3980.5 |  |  | Binghamton | Industrial Manufacturing | Binghamton Industrial Manufacturing | 0.4 | 0.4 | 0.26 | 0 | 0.335 |  |  | Tables 3-74 and 3-75: Power Part Load Ratios
Grocery |  |  |  | 125 | 95% | 94.1% | 95.4% | 95.4% | 95% | 95% | 94.1% | 94.1% | 125 | 95.4% | 95.4% | 95% | 95% | 94.1% | 94.1% | Binghamton | Institutional/Public Service | Binghamton Institutional/Public Service | #N/A | #N/A | #N/A | #N/A | 5223 |  |  | Binghamton | Institutional/Public Service | Binghamton Institutional/Public Service | #N/A | #N/A | #N/A | #N/A | 0.38 |  |  | Flow Fraction (%) | 0% | 10% | 20% | 30% | 40% | 50% | 60% | 70% | 80% | 90% | 100%
Health - Hospital |  |  |  | 150 | 95% | 94.1% | 95.8% | 95.8% | 95.8% | 95.4% | 94.1% | 94.1% | 150 | 95.8% | 95.8% | 95.8% | 95.4% | 94.1% | 94.1% | Binghamton | Lodging | Binghamton Lodging | 5042 | 5039 | 1733 | 7072 | 8760 |  |  | Binghamton | Lodging | Binghamton Lodging | 0.58 | 0.58 | 0.08 | 0 | 0.64 |  | 2 | VFD Fan | 0.0475 | 0.0475 | 0.0537 | 0.08 | 0.1289 | 0.2027 | 0.3038 | 0.4346 | 0.5975 | 0.795 | 1.0293
Health - Other |  |  |  | 200 | 95.4% | 95% | 96.2% | 95.8% | 95.8% | 95.4% | 94.5% | 94.1% | 200 | 96.2% | 95.8% | 95.8% | 95.4% | 94.5% | 94.1% | Binghamton | Office | Binghamton Office | 1401.5 | 1401.5 | 3546 | 3876 | 4472.5 |  |  | Binghamton | Office | Binghamton Office | 0.245 | 0.245 | 0.37 | 0 | 0.255 |  | 3 | VFD Pump | 0.27448 | 0.19124 | 0.14325 | 0.1305 | 0.15298 | 0.21071 | 0.30368 | 0.43188 | 0.59533 | 0.79402 | 1.0279
Industrial Manufacturing |  |  |  | 250 | 95.8% | 95% | 96.2% | 95.8% | 95.8% | 95.8% | 95% | 95% | Custom 1 | Edit | Edit | Edit | Edit | Edit | Edit | Binghamton | Restaurant | Binghamton Restaurant | #N/A | #N/A | #N/A | #N/A | 2679.5 |  |  | Binghamton | Restaurant | Binghamton Restaurant | #N/A | #N/A | #N/A | #N/A | 0.185 |  | 4 | Fan: Forward Curved with Inlet Guide Vanes | 0.2 | 0.20643 | 0.2157 | 0.2332 | 0.26435 | 0.31454 | 0.38917 | 0.49364 | 0.63334 | 0.81369 | 1.0401
Institutional/Public Service |  |  |  | 300 | 95.8% | 95.4% | 96.2% | 95.8% | 95.8% | 95.8% | N/A | N/A | Custom 2 | Edit | Edit | Edit | Edit | Edit | Edit | Binghamton | Retail | Binghamton Retail | 2416 | 2416 | 3100 | 3183 | 5188 |  |  | Binghamton | Retail | Binghamton Retail | 0.33 | 0.33 | 0.2 | 0 | 0.4 |  | 5 | Fan: Air Foil / Backward Incline with Inlet Guide Vanes | 0.47262 | 0.52642 | 0.55755 | 0.57439 | 0.58535 | 0.59884 | 0.62324 | 0.66697 | 0.73841 | 0.84597 | 0.99806
Lodging |  |  |  | 350 | 95.8% | 95.4% | 96.2% | 95.8% | 95.8% | 95.8% | N/A | N/A | Custom 3 | Edit | Edit | Edit | Edit | Edit | Edit | Binghamton | Warehouse - Other | Binghamton Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 5189 |  |  | Binghamton | Warehouse - Other | Binghamton Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 0.11 |  | 6 | Fan: Two-Speed CT Fan | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1
Office |  |  |  | 400 | 95.8% | 95.8% | 96.2% | 95.8% | N/A | N/A | N/A | N/A | [7 empty] | Binghamton | Warehouse - Refrigerated | Binghamton Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 4041 |  |  | Binghamton | Warehouse - Refrigerated | Binghamton Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 0.46 |  | 7 | Fan: Forward Curved | 0.20419 | 0.22262 | 0.25596 | 0.30419 | 0.36732 | 0.44536 | 0.53829 | 0.64612 | 0.76885 | 0.90649 | 1.059
Restaurant |  |  |  | 450 | 95.8% | 96.2% | 96.2% | 96.2% | N/A | N/A | N/A | N/A | [7 empty] | Bradford | Education - College/University | Bradford Education - College/University | 3096 | 3095.5 | 3939 | 5900 | 6126 |  |  | Bradford | Education - College/University | Bradford Education - College/University | 0.225 | 0.225 | 0.53 | 0.005 | 0.235 |  | 8 | Fan: Air Foil / Backward Incline | 0.55929 | 0.5256 | 0.53276 | 0.57235 | 0.63599 | 0.71526 | 0.80178 | 0.88713 | 0.96293 | 1.0208 | 1.0522
Retail |  |  |  | 500 | 95.8% | 96.2% | 96.2% | 96.2% | N/A | N/A | N/A | N/A | [7 empty] | Bradford | Education - Other | Bradford Education - Other | 1631 | 1634 | 1084 | 4722 | 4718 |  |  | Bradford | Education - Other | Bradford Education - Other | 0.07 | 0.07 | 0.32 | 0 | 0.066667 |  | 9 | Fan: Constant Volume | bar: 0% to 100%
Warehouse - Other |  |  |  | Custom 1 | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit | [7 empty] | Bradford | Grocery | Bradford Grocery | #N/A | #N/A | #N/A | #N/A | 6810 |  |  | Bradford | Grocery | Bradford Grocery | #N/A | #N/A | #N/A | #N/A | 0.19 |  |  | Pump: Throttle Valve | 0.55212 | 0.61392 | 0.67192 | 0.72612 | 0.77652 | 0.82312 | 0.86592 | 0.90492 | 0.94012 | 0.97152 | 0.99912
Warehouse - Refrigerated |  |  |  | Custom 2 | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit | [7 empty] | Bradford | Health - Hospital | Bradford Health - Hospital | 4167 | 4165 | 1177 | 8760 | 8760 |  |  | Bradford | Health - Hospital | Bradford Health - Hospital | 0.31 | 0.31 | 0.2 | 0.09 | 0.29 |  |  | Pump: Constant Volume | bar: 0% to 100%
|  |  |  | Custom 3 | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit | [7 empty] | Bradford | Health - Other | Bradford Health - Other | 2592 | 2593 | 1986 | 7170 | 8760 |  |  | Bradford | Health - Other | Bradford Health - Other | 0.16 | 0.16 | 0.28 | 0 | 0.17
[20 empty] | Bradford | Industrial Manufacturing | Bradford Industrial Manufacturing | 1086 | 1086 | 2465.5 | 1944 | 4080 |  |  | Bradford | Industrial Manufacturing | Bradford Industrial Manufacturing | 0.32 | 0.32 | 0.195 | 0 | 0.28
[20 empty] | Bradford | Institutional/Public Service | Bradford Institutional/Public Service | #N/A | #N/A | #N/A | #N/A | 5248 |  |  | Bradford | Institutional/Public Service | Bradford Institutional/Public Service | #N/A | #N/A | #N/A | #N/A | 0.34
[20 empty] | Bradford | Lodging | Bradford Lodging | 4444 | 4442 | 1529 | 7587 | 8760 |  |  | Bradford | Lodging | Bradford Lodging | 0.53 | 0.53 | 0.07 | 0 | 0.6
|  |  |  | Baseline Control Types | [15 empty] | Bradford | Office | Bradford Office | 1188.5 | 1188.5 | 3293 | 4445.5 | 4698.5 |  |  | Bradford | Office | Bradford Office | 0.2 | 0.2 | 0.29 | 0 | 0.21
|  |  |  | Fan: Constant Volume | [15 empty] | Bradford | Restaurant | Bradford Restaurant | #N/A | #N/A | #N/A | #N/A | 6486.5 |  |  | Bradford | Restaurant | Bradford Restaurant | #N/A | #N/A | #N/A | #N/A | 0.28
|  |  |  | Fan: Air Foil / Backward Incline | [15 empty] | Bradford | Retail | Bradford Retail | 2012 | 2012 | 2585 | 3568 | 5234 |  |  | Bradford | Retail | Bradford Retail | 0.28 | 0.28 | 0.16 | 0 | 0.35667
|  |  |  | Fan: Air Foil / Backward Incline with Inlet Guide Vanes | [15 empty] | Bradford | Warehouse - Other | Bradford Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 5259 |  |  | Bradford | Warehouse - Other | Bradford Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 0.1
|  |  |  | Fan: Forward Curved | [15 empty] | Bradford | Warehouse - Refrigerated | Bradford Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 4041 |  |  | Bradford | Warehouse - Refrigerated | Bradford Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 0.43
|  |  |  | Fan: Forward Curved with Inlet Guide Vanes | [15 empty] | Erie | Education - College/University | Erie Education - College/University | 3641 | 3640.5 | 4766 | 5036 | 6138.5 |  |  | Erie | Education - College/University | Erie Education - College/University | 0.295 | 0.295 | 0.61 | 0.005 | 0.315
NEMA Design Types | [19 empty] | Erie | Education - Other | Erie Education - Other | 2175 | 2178 | 1445 | 4080 | 4572 |  |  | Erie | Education - Other | Erie Education - Other | 0.09 | 0.09 | 0.43 | 0 | 0.09
NEMA Design A | [19 empty] | Erie | Grocery | Erie Grocery | #N/A | #N/A | #N/A | #N/A | 6738 |  |  | Erie | Grocery | Erie Grocery | #N/A | #N/A | #N/A | #N/A | 0.22
NEMA Design B |  |  |  | Pump: Chilled Water Pump | [15 empty] | Erie | Health - Hospital | Erie Health - Hospital | 5109 | 5107 | 1569 | 8760 | 8760 |  |  | Erie | Health - Hospital | Erie Health - Hospital | 0.42 | 0.41 | 0.27 | 0.09 | 0.39
NEMA Design C |  |  |  | Pump: Hot Water Pump | [15 empty] | Erie | Health - Other | Erie Health - Other | 3456 | 3457 | 2616 | 6280 | 8760 |  |  | Erie | Health - Other | Erie Health - Other | 0.22 | 0.22 | 0.38 | 0 | 0.23
[20 empty] | Erie | Industrial Manufacturing | Erie Industrial Manufacturing | 1448 | 1448 | 3063 | 1555 | 3977 |  |  | Erie | Industrial Manufacturing | Erie Industrial Manufacturing | 0.43 | 0.43 | 0.295 | 0 | 0.375
[20 empty] | Erie | Institutional/Public Service | Erie Institutional/Public Service | #N/A | #N/A | #N/A | #N/A | 5217 |  |  | Erie | Institutional/Public Service | Erie Institutional/Public Service | #N/A | #N/A | #N/A | #N/A | 0.45
City | [19 empty] | Erie | Lodging | Erie Lodging | 5198 | 5197 | 2039 | 6829 | 8760 |  |  | Erie | Lodging | Erie Lodging | 0.6 | 0.61 | 0.09 | 0 | 0.65
Allentown | [19 empty] | Erie | Office | Erie Office | 1584.5 | 1584.5 | 3698 | 3610.5 | 4440.5 |  |  | Erie | Office | Erie Office | 0.27 | 0.27 | 0.41 | 0 | 0.28
Binghamton | [19 empty] | Erie | Restaurant | Erie Restaurant | #N/A | #N/A | #N/A | #N/A | 6365 |  |  | Erie | Restaurant | Erie Restaurant | #N/A | #N/A | #N/A | #N/A | 0.37
Bradford | [19 empty] | Erie | Retail | Erie Retail | 2653 | 2653 | 3394 | 2960 | 5158 |  |  | Erie | Retail | Erie Retail | 0.38 | 0.38 | 0.22 | 0 | 0.43667
Erie | [19 empty] | Erie | Warehouse - Other | Erie Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 5222 |  |  | Erie | Warehouse - Other | Erie Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 0.13
Harrisburg | [19 empty] | Erie | Warehouse - Refrigerated | Erie Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 4041 |  |  | Erie | Warehouse - Refrigerated | Erie Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 0.48
Philadelphia | [19 empty] | Harrisburg | Education - College/University | Harrisburg Education - College/University | 4057 | 4056.5 | 5569 | 4250 | 5860 |  |  | Harrisburg | Education - College/University | Harrisburg Education - College/University | 0.415 | 0.415 | 0.67 | 0 | 0.44
Pittsburgh | [19 empty] | Harrisburg | Education - Other | Harrisburg Education - Other | 2730 | 2744 | 1737 | 3492 | 4313.3333 |  |  | Harrisburg | Education - Other | Harrisburg Education - Other | 0.18 | 0.18 | 0.54 | 0 | 0.17333
Scranton | [19 empty] | Harrisburg | Grocery | Harrisburg Grocery | #N/A | #N/A | #N/A | #N/A | 6692 |  |  | Harrisburg | Grocery | Harrisburg Grocery | #N/A | #N/A | #N/A | #N/A | 0.24
Williamsburg | [19 empty] | Harrisburg | Health - Hospital | Harrisburg Health - Hospital | 5717 | 5714 | 1792 | 8760 | 8760 |  |  | Harrisburg | Health - Hospital | Harrisburg Health - Hospital | 0.5 | 0.49 | 0.345 | 0.09 | 0.45
[20 empty] | Harrisburg | Health - Other | Harrisburg Health - Other | 4104 | 4106 | 3025 | 5823 | 8760 |  |  | Harrisburg | Health - Other | Harrisburg Health - Other | 0.28 | 0.28 | 0.53 | 0 | 0.29
[20 empty] | Harrisburg | Industrial Manufacturing | Harrisburg Industrial Manufacturing | 1742 | 1742 | 3602 | 1184 | 3768.5 |  |  | Harrisburg | Industrial Manufacturing | Harrisburg Industrial Manufacturing | 0.53 | 0.54 | 0.415 | 0 | 0.53
[20 empty] | Harrisburg | Institutional/Public Service | Harrisburg Institutional/Public Service | #N/A | #N/A | #N/A | #N/A | 5172 |  |  | Harrisburg | Institutional/Public Service | Harrisburg Institutional/Public Service | #N/A | #N/A | #N/A | #N/A | 0.6
[20 empty] | Harrisburg | Lodging | Harrisburg Lodging | 6045 | 6043 | 2539 | 6155 | 8760 |  |  | Harrisburg | Lodging | Harrisburg Lodging | 0.66 | 0.67 | 0.18 | 0 | 0.71
[20 empty] | Harrisburg | Office | Harrisburg Office | 1804 | 1804 | 3687 | 3014 | 4087 |  |  | Harrisburg | Office | Harrisburg Office | 0.345 | 0.345 | 0.49 | 0 | 0.37
[20 empty] | Harrisburg | Restaurant | Harrisburg Restaurant | #N/A | #N/A | #N/A | #N/A | 6251.5 |  |  | Harrisburg | Restaurant | Harrisburg Restaurant | #N/A | #N/A | #N/A | #N/A | 0.42
[20 empty] | Harrisburg | Retail | Harrisburg Retail | 3085 | 3085 | 3725 | 2561 | 5108.3333 |  |  | Harrisburg | Retail | Harrisburg Retail | 0.53 | 0.53 | 0.28 | 0 | 0.52667
[20 empty] | Harrisburg | Warehouse - Other | Harrisburg Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 4980 |  |  | Harrisburg | Warehouse - Other | Harrisburg Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 0.24
[20 empty] | Harrisburg | Warehouse - Refrigerated | Harrisburg Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 4041 |  |  | Harrisburg | Warehouse - Refrigerated | Harrisburg Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 0.52
[20 empty] | Philadelphia | Education - College/University | Philadelphia Education - College/University | 4310.5 | 4309 | 5886 | 4014 | 5965.5 |  |  | Philadelphia | Education - College/University | Philadelphia Education - College/University | 0.445 | 0.445 | 0.68 | 0 | 0.465
[20 empty] | Philadelphia | Education - Other | Philadelphia Education - Other | 3505 | 3517 | 1889 | 3341 | 4384 |  |  | Philadelphia | Education - Other | Philadelphia Education - Other | 0.18 | 0.18 | 0.59 | 0 | 0.18
[20 empty] | Philadelphia | Grocery | Philadelphia Grocery | #N/A | #N/A | #N/A | #N/A | 6669 |  |  | Philadelphia | Grocery | Philadelphia Grocery | #N/A | #N/A | #N/A | #N/A | 0.26
[20 empty] | Philadelphia | Health - Hospital | Philadelphia Health - Hospital | 6086 | 6084 | 2027 | 8760 | 8760 |  |  | Philadelphia | Health - Hospital | Philadelphia Health - Hospital | 0.54 | 0.54 | 0.36 | 0.09 | 0.51
[20 empty] | Philadelphia | Health - Other | Philadelphia Health - Other | 4535 | 4537 | 3185 | 5477 | 8760 |  |  | Philadelphia | Health - Other | Philadelphia Health - Other | 0.3 | 0.3 | 0.54 | 0 | 0.31
[20 empty] | Philadelphia | Industrial Manufacturing | Philadelphia Industrial Manufacturing | 1891 | 1891 | 4029.5 | 1028 | 3838 |  |  | Philadelphia | Industrial Manufacturing | Philadelphia Industrial Manufacturing | 0.58 | 0.59 | 0.445 | 0 | 0.565
[20 empty] | Philadelphia | Institutional/Public Service | Philadelphia Institutional/Public Service | #N/A | #N/A | #N/A | #N/A | 5186 |  |  | Philadelphia | Institutional/Public Service | Philadelphia Institutional/Public Service | #N/A | #N/A | #N/A | #N/A | 0.72
[20 empty] | Philadelphia | Lodging | Philadelphia Lodging | 6161 | 6159 | 3346 | 6077 | 8760 |  |  | Philadelphia | Lodging | Philadelphia Lodging | 0.67 | 0.68 | 0.18 | 0 | 0.71
[20 empty] | Philadelphia | Office | Philadelphia Office | 2036 | 2036 | 4168 | 2689.5 | 4063 |  |  | Philadelphia | Office | Philadelphia Office | 0.36 | 0.36 | 0.54 | 0 | 0.385
[20 empty] | Philadelphia | Restaurant | Philadelphia Restaurant | #N/A | #N/A | #N/A | #N/A | 6225.5 |  |  | Philadelphia | Restaurant | Philadelphia Restaurant | #N/A | #N/A | #N/A | #N/A | 0.5
[20 empty] | Philadelphia | Retail | Philadelphia Retail | 3225 | 3226 | 4304 | 2398 | 5092.3333 |  |  | Philadelphia | Retail | Philadelphia Retail | 0.54 | 0.54 | 0.3 | 0 | 0.56333
[20 empty] | Philadelphia | Warehouse - Other | Philadelphia Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 5168 |  |  | Philadelphia | Warehouse - Other | Philadelphia Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 0.3
[20 empty] | Philadelphia | Warehouse - Refrigerated | Philadelphia Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 4041 |  |  | Philadelphia | Warehouse - Refrigerated | Philadelphia Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 0.53
[20 empty] | Pittsburgh | Education - College/University | Pittsburgh Education - College/University | 3915.5 | 3913.5 | 5239 | 4572 | 5982 |  |  | Pittsburgh | Education - College/University | Pittsburgh Education - College/University | 0.395 | 0.395 | 0.7 | 0.005 | 0.415
[20 empty] | Pittsburgh | Education - Other | Pittsburgh Education - Other | 2676 | 2685 | 1602 | 3705 | 4415.3333 |  |  | Pittsburgh | Education - Other | Pittsburgh Education - Other | 0.17 | 0.17 | 0.54 | 0 | 0.18
[20 empty] | Pittsburgh | Grocery | Pittsburgh Grocery | #N/A | #N/A | #N/A | #N/A | 6718 |  |  | Pittsburgh | Grocery | Pittsburgh Grocery | #N/A | #N/A | #N/A | #N/A | 0.29
[20 empty] | Pittsburgh | Health - Hospital | Pittsburgh Health - Hospital | 5593 | 5591 | 1729.5 | 8760 | 8760 |  |  | Pittsburgh | Health - Hospital | Pittsburgh Health - Hospital | 0.48 | 0.47 | 0.325 | 0.09 | 0.45
[20 empty] | Pittsburgh | Health - Other | Pittsburgh Health - Other | 3900 | 3902 | 2757 | 5991 | 8760 |  |  | Pittsburgh | Health - Other | Pittsburgh Health - Other | 0.28 | 0.28 | 0.47 | 0 | 0.29
[20 empty] | Pittsburgh | Industrial Manufacturing | Pittsburgh Industrial Manufacturing | 1606 | 1606 | 3749 | 1287 | 3869 |  |  | Pittsburgh | Industrial Manufacturing | Pittsburgh Industrial Manufacturing | 0.54 | 0.54 | 0.395 | 0 | 0.495
[20 empty] | Pittsburgh | Institutional/Public Service | Pittsburgh Institutional/Public Service | #N/A | #N/A | #N/A | #N/A | 5201 |  |  | Pittsburgh | Institutional/Public Service | Pittsburgh Institutional/Public Service | #N/A | #N/A | #N/A | #N/A | 0.56
[20 empty] | Pittsburgh | Lodging | Pittsburgh Lodging | 5686 | 5683 | 2409 | 6574 | 8760 |  |  | Pittsburgh | Lodging | Pittsburgh Lodging | 0.69 | 0.7 | 0.17 | 0 | 0.73
[20 empty] | Pittsburgh | Office | Pittsburgh Office | 1739 | 1739 | 4093 | 3245.5 | 4239.5 |  |  | Pittsburgh | Office | Pittsburgh Office | 0.325 | 0.325 | 0.47 | 0 | 0.345
[20 empty] | Pittsburgh | Restaurant | Pittsburgh Restaurant | #N/A | #N/A | #N/A | #N/A | 6299.5 |  |  | Pittsburgh | Restaurant | Pittsburgh Restaurant | #N/A | #N/A | #N/A | #N/A | 0.49
[20 empty] | Pittsburgh | Retail | Pittsburgh Retail | 2795 | 2795 | 3571 | 2908 | 5146.3333 |  |  | Pittsburgh | Retail | Pittsburgh Retail | 0.47 | 0.47 | 0.28 | 0 | 0.54
[20 empty] | Pittsburgh | Warehouse - Other | Pittsburgh Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 5110 |  |  | Pittsburgh | Warehouse - Other | Pittsburgh Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 0.23
[20 empty] | Pittsburgh | Warehouse - Refrigerated | Pittsburgh Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 4041 |  |  | Pittsburgh | Warehouse - Refrigerated | Pittsburgh Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 0.51
[20 empty] | Scranton | Education - College/University | Scranton Education - College/University | 3827.5 | 3826.5 | 5353 | #REF! | 5876 |  |  | Scranton | Education - College/University | Scranton Education - College/University | 0.33 | 0.33 | 0.59 | 0.005 | 0.38
[20 empty] | Scranton | Education - Other | Scranton Education - Other | 2310 | 2313 | 1558 | #REF! | 4490.3333 |  |  | Scranton | Education - Other | Scranton Education - Other | 0.12 | 0.12 | 0.48 | 0 | 0.12333
[20 empty] | Scranton | Grocery | Scranton Grocery | #N/A | #N/A | #N/A | #N/A | 6725 |  |  | Scranton | Grocery | Scranton Grocery | #N/A | #N/A | #N/A | #N/A | 0.21
[20 empty] | Scranton | Health - Hospital | Scranton Health - Hospital | 5266 | 5263 | 1630.5 | #REF! | 8760 |  |  | Scranton | Health - Hospital | Scranton Health - Hospital | 0.44 | 0.44 | 0.29 | 0.09 | 0.4
[20 empty] | Scranton | Health - Other | Scranton Health - Other | 3710 | 3711 | 2702 | #REF! | 8760 |  |  | Scranton | Health - Other | Scranton Health - Other | 0.23 | 0.23 | 0.42 | 0 | 0.25
[20 empty] | Scranton | Industrial Manufacturing | Scranton Industrial Manufacturing | 1558 | 1558 | 3500 | #REF! | 3901.5 |  |  | Scranton | Industrial Manufacturing | Scranton Industrial Manufacturing | 0.48 | 0.48 | 0.33 | 0 | 0.43
[20 empty] | Scranton | Institutional/Public Service | Scranton Institutional/Public Service | #N/A | #N/A | #N/A | #N/A | 5207 |  |  | Scranton | Institutional/Public Service | Scranton Institutional/Public Service | #N/A | #N/A | #N/A | #N/A | 0.47
[20 empty] | Scranton | Lodging | Scranton Lodging | 5655 | 5652 | 2164 | #REF! | 8760 |  |  | Scranton | Lodging | Scranton Lodging | 0.59 | 0.59 | 0.12 | 0 | 0.65
[20 empty] | Scranton | Office | Scranton Office | 1637.5 | 1637.5 | 3713 | #REF! | 4227.5 |  |  | Scranton | Office | Scranton Office | 0.29 | 0.29 | 0.44 | 0 | 0.32
[20 empty] | Scranton | Restaurant | Scranton Restaurant | #N/A | #N/A | #N/A | #N/A | 6315 |  |  | Scranton | Restaurant | Scranton Restaurant | #N/A | #N/A | #N/A | #N/A | 0.39
[20 empty] | Scranton | Retail | Scranton Retail | 2735 | 2736 | 3687 | #REF! | 5148.6667 |  |  | Scranton | Retail | Scranton Retail | 0.42 | 0.42 | 0.23 | 0 | 0.45333
[20 empty] | Scranton | Warehouse - Other | Scranton Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 5188 |  |  | Scranton | Warehouse - Other | Scranton Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 0.15
[20 empty] | Scranton | Warehouse - Refrigerated | Scranton Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 4041 |  |  | Scranton | Warehouse - Refrigerated | Scranton Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 0.48
[20 empty] | Scranton | Education - College/University | Scranton Education - College/University | 3827.5 | 3826.5 | 5353 | #REF! | 5876 |  |  | Scranton | Education - College/University | Scranton Education - College/University | 0.33 | 0.33 | 0.59 | 0.005 | 0.38
[20 empty] | Scranton | Education - Other | Scranton Education - Other | 2310 | 2313 | 1558 | #REF! | 4490.3333 |  |  | Scranton | Education - Other | Scranton Education - Other | 0.12 | 0.12 | 0.48 | 0 | 0.12333
[20 empty] | Scranton | Grocery | Scranton Grocery | #N/A | #N/A | #N/A | #N/A | 6725 |  |  | Scranton | Grocery | Scranton Grocery | #N/A | #N/A | #N/A | #N/A | 0.21
[20 empty] | Scranton | Health - Hospital | Scranton Health - Hospital | 5266 | 5263 | 1630.5 | #REF! | 8760 |  |  | Scranton | Health - Hospital | Scranton Health - Hospital | 0.44 | 0.44 | 0.29 | 0.09 | 0.4
[20 empty] | Scranton | Health - Other | Scranton Health - Other | 3710 | 3711 | 2702 | #REF! | 8760 |  |  | Scranton | Health - Other | Scranton Health - Other | 0.23 | 0.23 | 0.42 | 0 | 0.25
[20 empty] | Scranton | Industrial Manufacturing | Scranton Industrial Manufacturing | 1558 | 1558 | 3500 | #REF! | 3901.5 |  |  | Scranton | Industrial Manufacturing | Scranton Industrial Manufacturing | 0.48 | 0.48 | 0.33 | 0 | 0.43
[20 empty] | Scranton | Institutional/Public Service | Scranton Institutional/Public Service | #N/A | #N/A | #N/A | #N/A | 5207 |  |  | Scranton | Institutional/Public Service | Scranton Institutional/Public Service | #N/A | #N/A | #N/A | #N/A | 0.47
[20 empty] | Scranton | Lodging | Scranton Lodging | 5655 | 5652 | 2164 | #REF! | 8760 |  |  | Scranton | Lodging | Scranton Lodging | 0.59 | 0.59 | 0.12 | 0 | 0.65
[20 empty] | Scranton | Office | Scranton Office | 1637.5 | 1637.5 | 3713 | #REF! | 4227.5 |  |  | Scranton | Office | Scranton Office | 0.29 | 0.29 | 0.44 | 0 | 0.32
[20 empty] | Scranton | Restaurant | Scranton Restaurant | #N/A | #N/A | #N/A | #N/A | 6315 |  |  | Scranton | Restaurant | Scranton Restaurant | #N/A | #N/A | #N/A | #N/A | 0.39
[20 empty] | Scranton | Retail | Scranton Retail | 2735 | 2736 | 3687 | #REF! | 5148.6667 |  |  | Scranton | Retail | Scranton Retail | 0.42 | 0.42 | 0.23 | 0 | 0.45333
[20 empty] | Scranton | Warehouse - Other | Scranton Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 5188 |  |  | Scranton | Warehouse - Other | Scranton Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 0.15
[20 empty] | Scranton | Warehouse - Refrigerated | Scranton Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 4041 |  |  | Scranton | Warehouse - Refrigerated | Scranton Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 0.48
[20 empty] | Williamsburg | Education - College/University | Williamsburg Education - College/University | 3871.5 | 3871 | 5328 | #REF! | 5904.5 |  |  | Williamsburg | Education - College/University | Williamsburg Education - College/University | 0.395 | 0.39 | 0.66 | 0.005 | 0.435
[20 empty] | Williamsburg | Education - Other | Williamsburg Education - Other | 2573 | 2604 | 1632 | #REF! | 4376.6667 |  |  | Williamsburg | Education - Other | Williamsburg Education - Other | 0.16 | 0.17 | 0.5 | 0 | 0.14667
[20 empty] | Williamsburg | Grocery | Williamsburg Grocery | #N/A | #N/A | #N/A | #N/A | 6710 |  |  | Williamsburg | Grocery | Williamsburg Grocery | #N/A | #N/A | #N/A | #N/A | 0.24
[20 empty] | Williamsburg | Health - Hospital | Williamsburg Health - Hospital | 5628 | 5626 | 1702 | #REF! | 8760 |  |  | Williamsburg | Health - Hospital | Williamsburg Health - Hospital | 0.47 | 0.46 | 0.32 | 0.09 | 0.41
[20 empty] | Williamsburg | Health - Other | Williamsburg Health - Other | 3818 | 3819 | 2847 | #REF! | 8760 |  |  | Williamsburg | Health - Other | Williamsburg Health - Other | 0.26 | 0.26 | 0.47 | 0 | 0.28
[20 empty] | Williamsburg | Industrial Manufacturing | Williamsburg Industrial Manufacturing | 1633 | 1633 | 3489 | #REF! | 3828.5 |  |  | Williamsburg | Industrial Manufacturing | Williamsburg Industrial Manufacturing | 0.5 | 0.5 | 0.39 | 0 | 0.46
[20 empty] | Williamsburg | Institutional/Public Service | Williamsburg Institutional/Public Service | #N/A | #N/A | #N/A | #N/A | 5184 |  |  | Williamsburg | Institutional/Public Service | Williamsburg Institutional/Public Service | #N/A | #N/A | #N/A | #N/A | 0.52
[20 empty] | Williamsburg | Lodging | Williamsburg Lodging | 5776 | 5773 | 2423 | #REF! | 8760 |  |  | Williamsburg | Lodging | Williamsburg Lodging | 0.66 | 0.66 | 0.17 | 0 | 0.71
[20 empty] | Williamsburg | Office | Williamsburg Office | 1710.5 | 1710.5 | 3670 | #REF! | 4138.5 |  |  | Williamsburg | Office | Williamsburg Office | 0.32 | 0.32 | 0.46 | 0 | 0.34
[20 empty] | Williamsburg | Restaurant | Williamsburg Restaurant | #N/A | #N/A | #N/A | #N/A | 6285.5 |  |  | Williamsburg | Restaurant | Williamsburg Restaurant | #N/A | #N/A | #N/A | #N/A | 0.45
[20 empty] | Williamsburg | Retail | Williamsburg Retail | 2898 | 2898 | 3722 | #REF! | 5133.6667 |  |  | Williamsburg | Retail | Williamsburg Retail | 0.47 | 0.47 | 0.26 | 0 | 0.48667
[20 empty] | Williamsburg | Warehouse - Other | Williamsburg Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 5028 |  |  | Williamsburg | Warehouse - Other | Williamsburg Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 0.2
[20 empty] | Williamsburg | Warehouse - Refrigerated | Williamsburg Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 4041 |  |  | Williamsburg | Warehouse - Refrigerated | Williamsburg Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 0.51
[20 empty] | SF/RF | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg |  | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg
[20 empty] | Education - College/University | 6041.5 | 6054 | 6126 | 6138.5 | 5860 | 5965.5 | 5982 | 5876 | 5904.5 | Education - College/University | 0.425 | 0.3 | 0.235 | 0.315 | 0.44 | 0.465 | 0.415 | 0.38 | 0.435
[20 empty] | Education - Other | 4380 | 4583 | 4718 | 4572 | 4313.3333 | 4384 | 4415.3333 | 4490.3333 | 4376.6667 | Education - Other | 0.12 | 0.08 | 0.066667 | 0.09 | 0.17333 | 0.18 | 0.18 | 0.12333 | 0.14667
[20 empty] | Grocery | 6708 | 6764 | 6810 | 6738 | 6692 | 6669 | 6718 | 6725 | 6710 | Grocery | 0.24 | 0.21 | 0.19 | 0.22 | 0.24 | 0.26 | 0.29 | 0.21 | 0.24
[20 empty] | Health - Hospital | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | Health - Hospital | 0.43 | 0.24 | 0.29 | 0.39 | 0.45 | 0.51 | 0.45 | 0.4 | 0.41
[20 empty] | Health - Other | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | Health - Other | 0.24 | 0.21 | 0.17 | 0.23 | 0.29 | 0.31 | 0.29 | 0.25 | 0.28
[20 empty] | Industrial Manufacturing | 3831 | 3980.5 | 4080 | 3977 | 3768.5 | 3838 | 3869 | 3901.5 | 3828.5 | Industrial Manufacturing | 0.475 | 0.335 | 0.28 | 0.375 | 0.53 | 0.565 | 0.495 | 0.43 | 0.46
[20 empty] | Institutional/Public Service | 5188 | 5223 | 5248 | 5217 | 5172 | 5186 | 5201 | 5207 | 5184 | Institutional/Public Service | 0.53 | 0.38 | 0.34 | 0.45 | 0.6 | 0.72 | 0.56 | 0.47 | 0.52
[20 empty] | Lodging | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | Lodging | 0.64 | 0.64 | 0.6 | 0.65 | 0.71 | 0.71 | 0.73 | 0.65 | 0.71
[20 empty] | Office | 4195 | 4472.5 | 4698.5 | 4440.5 | 4087 | 4063 | 4239.5 | 4227.5 | 4138.5 | Office | 0.295 | 0.255 | 0.21 | 0.28 | 0.37 | 0.385 | 0.345 | 0.32 | 0.34
[20 empty] | Restaurant | 6282 | 2679.5 | 6486.5 | 6365 | 6251.5 | 6225.5 | 6299.5 | 6315 | 6285.5 | Restaurant | 0.375 | 0.185 | 0.28 | 0.37 | 0.42 | 0.5 | 0.49 | 0.39 | 0.45
[20 empty] | Retail | 5136.6667 | 5188 | 5234 | 5158 | 5108.3333 | 5092.3333 | 5146.3333 | 5148.6667 | 5133.6667 | Retail | 0.50333 | 0.4 | 0.35667 | 0.43667 | 0.52667 | 0.56333 | 0.54 | 0.45333 | 0.48667
[20 empty] | Warehouse - Other | 5037 | 5189 | 5259 | 5222 | 4980 | 5168 | 5110 | 5188 | 5028 | Warehouse - Other | 0.18 | 0.11 | 0.1 | 0.13 | 0.24 | 0.3 | 0.23 | 0.15 | 0.2
[20 empty] | Warehouse - Refrigerated | 4041 | 4041 | 4041 | 4041 | 4041 | 4041 | 4041 | 4041 | 4041 | Warehouse - Refrigerated | 0.5 | 0.46 | 0.43 | 0.48 | 0.52 | 0.53 | 0.51 | 0.48 | 0.51
[20 empty] | CHW Pump | [9 empty] | CHW Pump
[20 empty] | Facility Type | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg | Facility Type | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg
[20 empty] | Education - College/University | 4006.5 | 3435.5 | 3096 | 3641 | 4057 | 4310.5 | 3915.5 | 3827.5 | 3871.5 | Education - College/University | 0.405 | 0.265 | 0.225 | 0.295 | 0.415 | 0.445 | 0.395 | 0.33 | 0.395
[20 empty] | Education - Other | 2721 | 1849 | 1631 | 2175 | 2730 | 3505 | 2676 | 2310 | 2573 | Education - Other | 0.1 | 0.08 | 0.07 | 0.09 | 0.18 | 0.18 | 0.17 | 0.12 | 0.16
[20 empty] | Health - Hospital | 5588 | 4801 | 4167 | 5109 | 5717 | 6086 | 5593 | 5266 | 5628 | Health - Hospital | 0.46 | 0.38 | 0.31 | 0.42 | 0.5 | 0.54 | 0.48 | 0.44 | 0.47
[20 empty] | Health - Other | 3892 | 3093 | 2592 | 3456 | 4104 | 4535 | 3900 | 3710 | 3818 | Health - Other | 0.24 | 0.2 | 0.16 | 0.22 | 0.28 | 0.3 | 0.28 | 0.23 | 0.26
[20 empty] | Industrial Manufacturing | 1735 | 1306 | 1086 | 1448 | 1742 | 1891 | 1606 | 1558 | 1633 | Industrial Manufacturing | 0.53 | 0.4 | 0.32 | 0.43 | 0.53 | 0.58 | 0.54 | 0.48 | 0.5
[20 empty] | Lodging | 5845 | 5042 | 4444 | 5198 | 6045 | 6161 | 5686 | 5655 | 5776 | Lodging | 0.61 | 0.58 | 0.53 | 0.6 | 0.66 | 0.67 | 0.69 | 0.59 | 0.66
[20 empty] | Office | 1789 | 1401.5 | 1188.5 | 1584.5 | 1804 | 2036 | 1739 | 1637.5 | 1710.5 | Office | 0.29 | 0.245 | 0.2 | 0.27 | 0.345 | 0.36 | 0.325 | 0.29 | 0.32
[20 empty] | Retail | 2957 | 2416 | 2012 | 2653 | 3085 | 3225 | 2795 | 2735 | 2898 | Retail | 0.46 | 0.33 | 0.28 | 0.38 | 0.53 | 0.54 | 0.47 | 0.42 | 0.47
[20 empty] | CT Fan | [9 empty] | CT Fan
[20 empty] | Facility Type | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg | Facility Type | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg
[20 empty] | Education - College/University | 4005.5 | 3435 | 3095.5 | 3640.5 | 4056.5 | 4309 | 3913.5 | 3826.5 | 3871 | Education - College/University | 0.405 | 0.26 | 0.225 | 0.295 | 0.415 | 0.445 | 0.395 | 0.33 | 0.39
[20 empty] | Education - Other | 2742 | 1851 | 1634 | 2178 | 2744 | 3517 | 2685 | 2313 | 2604 | Education - Other | 0.11 | 0.08 | 0.07 | 0.09 | 0.18 | 0.18 | 0.17 | 0.12 | 0.17
[20 empty] | Health - Hospital | 5587 | 4798 | 4165 | 5107 | 5714 | 6084 | 5591 | 5263 | 5626 | Health - Hospital | 0.45 | 0.37 | 0.31 | 0.41 | 0.49 | 0.54 | 0.47 | 0.44 | 0.46
[20 empty] | Health - Other | 3894 | 3093 | 2593 | 3457 | 4106 | 4537 | 3902 | 3711 | 3819 | Health - Other | 0.24 | 0.2 | 0.16 | 0.22 | 0.28 | 0.3 | 0.28 | 0.23 | 0.26
[20 empty] | Industrial Manufacturing | 1735 | 1306 | 1086 | 1448 | 1742 | 1891 | 1606 | 1558 | 1633 | Industrial Manufacturing | 0.53 | 0.4 | 0.32 | 0.43 | 0.54 | 0.59 | 0.54 | 0.48 | 0.5
[20 empty] | Lodging | 5844 | 5039 | 4442 | 5197 | 6043 | 6159 | 5683 | 5652 | 5773 | Lodging | 0.61 | 0.58 | 0.53 | 0.61 | 0.67 | 0.68 | 0.7 | 0.59 | 0.66
[20 empty] | Office | 1789 | 1401.5 | 1188.5 | 1584.5 | 1804 | 2036 | 1739 | 1637.5 | 1710.5 | Office | 0.29 | 0.245 | 0.2 | 0.27 | 0.345 | 0.36 | 0.325 | 0.29 | 0.32
[20 empty] | Retail | 2957 | 2416 | 2012 | 2653 | 3085 | 3226 | 2795 | 2736 | 2898 | Retail | 0.46 | 0.33 | 0.28 | 0.38 | 0.53 | 0.54 | 0.47 | 0.42 | 0.47
[20 empty] | HHW Pump | [9 empty] | HHW Pump
[20 empty] | Facility Type | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg | Facility Type | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg
[20 empty] | Education - College/University | 4548 | 5270.5 | 5900 | 5036 | 4250 | 4014 | 4572 | 4638 | 4487 | Education - College/University | 0.005 | 0.005 | 0.005 | 0.005 | 0 | 0 | 0.005 | 0.005 | 0.005
[20 empty] | Education - Other | 3651 | 4251 | 4722 | 4080 | 3492 | 3341 | 3705 | 3830 | 3658 | Education - Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | Health - Hospital | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | Health - Hospital | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09
[20 empty] | Health - Other | 5934 | 6627 | 7170 | 6280 | 5823 | 5477 | 5991 | 6223 | 6045 | Health - Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | Industrial Manufacturing | 1258 | 1684 | 1944 | 1555 | 1184 | 1028 | 1287 | 1393 | 1277 | Industrial Manufacturing | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | Lodging | 6469 | 7072 | 7587 | 6829 | 6155 | 6077 | 6574 | 6628 | 6387 | Lodging | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | Office | 3214 | 3876 | 4445.5 | 3610.5 | 3014 | 2689.5 | 3245.5 | 3336 | 3168.5 | Office | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | Retail | 2676 | 3183 | 3568 | 2960 | 2561 | 2398 | 2908 | 2841 | 2660 | Retail | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | Chiller 1 CW Pump | [9 empty] | Chiller 1 CW Pump
[20 empty] | Facility Type | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg | Facility Type | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg
[20 empty] | Lodging | 5544 | 4591 | 3939 | 4766 | 5569 | 5886 | 5239 | 5353 | 5328 | Lodging | 0.61 | 0.58 | 0.53 | 0.61 | 0.67 | 0.68 | 0.7 | 0.59 | 0.66
[20 empty] | Industrial Manufacturing | 1735 | 1305 | 1084 | 1445 | 1737 | 1889 | 1602 | 1558 | 1632 | Industrial Manufacturing | 0.53 | 0.4 | 0.32 | 0.43 | 0.54 | 0.59 | 0.54 | 0.48 | 0.5
[20 empty] | Office | 1781 | 1389 | 1177 | 1569 | 1792 | 2027 | 1729.5 | 1630.5 | 1702 | Office | 0.29 | 0.245 | 0.2 | 0.27 | 0.345 | 0.36 | 0.325 | 0.29 | 0.32
[20 empty] | Retail | 2889 | 2381 | 1986 | 2616 | 3025 | 3185 | 2757 | 2702 | 2847 | Retail | 0.46 | 0.33 | 0.28 | 0.38 | 0.53 | 0.54 | 0.47 | 0.42 | 0.47
[20 empty] | Education - College/University | 3527 | 2938 | 2465.5 | 3063 | 3602 | 4029.5 | 3749 | 3500 | 3489 | Education - College/University | 0.405 | 0.26 | 0.195 | 0.295 | 0.415 | 0.445 | 0.395 | 0.33 | 0.39
[20 empty] | Education - Other | 2448 | 1733 | 1529 | 2039 | 2539 | 3346 | 2409 | 2164 | 2423 | Education - Other | 0.11 | 0.08 | 0.07 | 0.09 | 0.18 | 0.18 | 0.17 | 0.12 | 0.17
[20 empty] | Health - Hospital | 3950 | 3546 | 3293 | 3698 | 3687 | 4168 | 4093 | 3713 | 3670 | Health - Hospital | 0.45 | 0.37 | 0.29 | 0.41 | 0.49 | 0.54 | 0.47 | 0.44 | 0.46
[20 empty] | Health - Other | 3675 | 3100 | 2585 | 3394 | 3725 | 4304 | 3571 | 3687 | 3722 | Health - Other | 0.24 | 0.2 | 0.16 | 0.22 | 0.28 | 0.3 | 0.28 | 0.23 | 0.26